## 0
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/0 |  |  | 2080/10/0 |  |  | 2080/10/0 |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 495.8 | 507.2 | 531.4 | 520.5 | 567.04 | 571.7 | 569.7 | 620.5 | 368.3 | 246.5 | 220.3 | 279.9 | 341.2 | 576.5 | 700.7 | 643.9 | 714.3 | 763.6 | 612.4 | 542.7 | 475.3 | 363.1 | 295.7 | 258.2 | 238.4 | 356.2 | 489.4 | 563 | 611.9 | 605.5 | 508.6
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1769MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1137 | 1163.14 | 1148.24 | 1159.94 | 1149.14 | 1137.44 | 1224.48 | 1335.64 | 1422.34 | 1556.44 | 1710.44 | 1769.34 | 1765.84 | 1631.74 | 1554.24 | 1357.34 | 1482.84 | 1395.24 | 1464.44 | 1464.04 | 1425.84 | 1295.24 | 1220.94 | 1393.14 | 1849.84 | 1781.54 | 1722.94 | 1706.19 | 1727.89 | 1690.29 | 1359.19 | 1223.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 28.9 | 27.2 | 27.2 | 26.9 | 27.2 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 86 | 30.5 | 26.9
Likhu-II(55) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 54 | 9.8 | 9.8
Super Dordi (54) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 54 | 12 | 10.3
Likhu-IV(52.4) | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 52.4 | 16.4 | 9
Upper Marsyangdi "A"(50) | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 50 | 29.8 | 28.3
Upper Bhotekoshi Khola(45) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 45 | 17.2 | 14.7
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14
Mistri Khola(42) | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 8.5 | 7.5
Upper Chameliya(40) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 15 | 12.2
Upper Kalanga Gad(38.46) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 10 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 30 | 8.8 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 8.6 | 7.2
Dordi(27) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 30 | 7.4 | 6.7
Upper Madi(25) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 25 | 8.9 | 8.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 25 | 8.1 | 7.4
Solu Khola(23.5) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 23.5 | 8.1 | 7.1
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 22 | 11.5 | 6.3
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.5
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 3.3 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 14.5 | 17.6 | 18.1 | 17.8 | 19 | 16.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 240 | 25 | 14.5
Total IPP | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 496.9 | 489.2 | 487.5 | 487.5 | 487.2 | 487.5 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 478.6 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 1042.4 | 496.9 | 478.6
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 75 | 120 | 260 | 420 | 405 | 225 | 125 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 30 | 210 | 345 | 340 | 350 | 235 | 200 | 100 | 0 | 0 | 456 | 420 | 0
Khimti Khola(60) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 30 | 30
Chilime(22.1) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 16 | 10.2 | 10.2 | 10.2 | 10.2 | 10 | 10 | 10 | 22.1 | 16 | 10
Total NEA SUBSIDIARIES | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 100.2 | 115.2 | 160.2 | 300.2 | 460.2 | 445.2 | 265.2 | 165.2 | 55.2 | 55.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 70.2 | 250.2 | 391 | 380.2 | 390.2 | 275.2 | 240.2 | 140 | 40 | 40 | 538.1 | 460.2 | 40
KGA(144) | 0 | 0 | 0 | 0 | 0 | 30.5 | 47 | 96.7 | 97.7 | 83.2 | 81.5 | 97.7 | 81.7 | 65.2 | 61.5 | 61.5 | 61.2 | 61.2 | 60.2 | 132.6 | 91.7 | 61.2 | 105.8 | 143.9 | 143.9 | 143 | 136.2 | 98 | 97 | 77 | 0 | 144 | 143.9 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 35 | 35 | 50 | 60 | 60 | 60 | 43 | 43 | 43 | 45 | 0 | 25 | 25 | 25 | 45 | 69 | 69 | 50 | 50 | 35 | 35 | 35 | 0 | 70 | 69 | 0
MRS(69) | 34.5 | 34.7 | 34.8 | 0 | 0 | 0 | 0 | 0 | 43.3 | 45.4 | 45.9 | 61.9 | 61.5 | 61.1 | 37.3 | 36.9 | 36.6 | 36.6 | 36.7 | 54.8 | 40.4 | 35.3 | 52.1 | 67.3 | 67.3 | 67.7 | 67.3 | 44 | 34 | 34 | 17 | 69 | 67.7 | 0
U Trisuli 3A(60) | 42.1 | 39.8 | 40 | 39.8 | 39 | 39 | 39 | 39 | 39 | 37.3 | 37.3 | 37.6 | 39.3 | 40.3 | 40 | 40 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 38 | 38 | 38 | 38 | 38 | 38 | 60 | 42.1 | 36.3
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 29 | 23 | 23 | 29 | 29 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 29 | 29 | 28 | 10 | 10 | 10 | 0 | 0 | 30 | 29 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 1.2 | 4.6 | 9.3 | 13.4 | 16.3 | 17.7 | 16.4 | 13.2 | 9.4 | 6.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17.7 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 14.1 | 9.9 | 8.4
MODI(14) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 14 | 4.5 | 3.4
SUN(10.05) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 10.05 | 2.5 | 2.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 117.44 | 115.34 | 115.64 | 80.64 | 79.84 | 120.34 | 166.84 | 240.54 | 278.84 | 265.04 | 285.74 | 331.14 | 319.14 | 280.34 | 238.44 | 239.44 | 232.54 | 231.34 | 181.64 | 294.64 | 233.74 | 196.84 | 301.24 | 384.54 | 384.54 | 365.74 | 340.54 | 264.04 | 253.04 | 223.04 | 94.04 | 489.91 | 384.54 | 79.84
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 71 | 68.1 | 63.8 | 60.5 | 64.8 | 64.9 | 75 | 76.8 | 65.4 | 71 | 61.5 | 49.3 | 39.7 | 46.4 | 55.6 | 57 | 58.9 | 65.4 | 68.8 | 63.7 | 68.4 | 63.9 | 55.5 | 64.4 | 47.7 | 34.3 | 49.1 | 56.2 | 59 | 59.7 | 54.5 |  | 76.8 | 34.3
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 404 | 391.1 | 405.8 | 434 | 417.6 | 430 | 425.6 | 415.3 | 405 | 173.9 | 64.3 | 52.6 | 143.4 | 203.2 | 410.9 | 430.2 | 402.8 | 417 | 456.4 | 425.9 | 387 | 339 | 231 | 145.5 | 127.1 | 121.5 | 215 | 338 | 397 | 421 | 427 |  | 456.4 | 52.6
RAMNAGAR | 15.6 | 15.6 | 16 | 15.5 | 16.5 | 49.74 | 49.5 | 54.8 | 52.7 | 21 | 17.6 | 17.1 | 16.3 | 16.3 | 31.4 | 45 | 47 | 51.8 | 48.2 | 43.8 | 20.6 | 11.6 | 11.5 | 13.3 | 13.1 | 16 | 23.1 | 27.8 | 38 | 54 | 42 |  | 54.8 | 11.5
RAXAUL 132 | 18 | 21 | 21.6 | 21.4 | 21.6 | 22.4 | 21.6 | 22.8 | 23.2 | 23.6 | 25 | 26.8 | 10.8 | 11.4 | 12.4 | 98 | 58.3 | 111.8 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 |  | 113 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2 | 78.8 | 78.1 | 74.5 | 69.7 | 63.9 | 66.2 | 70.5 | 76.9 | 68.3 | 77.2 | 79 | 66.7 | 60.8 | 65.1 | 72.5 | 70.3 | 66.6 | 69 | 67.4 | 69 | 77.2 | 66 |  | 79 | 0
Total IMPORT | 508.6 | 495.8 | 507.2 | 531.4 | 520.5 | 567.04 | 571.7 | 569.7 | 620.5 | 368.3 | 246.5 | 220.3 | 279.9 | 341.2 | 576.5 | 700.7 | 643.9 | 714.3 | 763.6 | 612.4 | 542.7 | 475.3 | 363.1 | 295.7 | 258.2 | 238.4 | 356.2 | 489.4 | 563 | 611.9 | 605.5 | 0 | 763.6 | 220.3
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1163.14 | 1148.24 | 1159.94 | 1149.14 | 1137.44 | 1224.48 | 1335.64 | 1422.34 | 1556.44 | 1430.44 | 1489.34 | 1485.84 | 1351.74 | 1274.24 | 1357.34 | 1482.84 | 1395.24 | 1464.44 | 1464.04 | 1425.84 | 1295.24 | 1220.94 | 1393.14 | 1549.84 | 1501.54 | 1472.94 | 1456.19 | 1477.89 | 1440.29 | 1359.19 | 1223.79 | 2231.81 | 1556.44 | 1137.44
Interruption/Tripping | 0.29167: 280; 0.3125: 280; 0.33333: 280; 0.375: 280; 0.41667: 280; 0.77083: 300; 0.79167: 280; 0.8125: 250; 0.83333: 250; 0.85417: 250; 0.875: 250 |  | 300 | 250
TOTAL SYSTEM LOAD (EXPECTED) | 1163.14 | 1148.24 | 1159.94 | 1149.14 | 1137.44 | 1224.48 | 1335.64 | 1422.34 | 1556.44 | 1710.44 | 1769.34 | 1765.84 | 1631.74 | 1554.24 | 1357.34 | 1482.84 | 1395.24 | 1464.44 | 1464.04 | 1425.84 | 1295.24 | 1220.94 | 1393.14 | 1849.84 | 1781.54 | 1722.94 | 1706.19 | 1727.89 | 1690.29 | 1359.19 | 1223.79 | 1693.71 | 1849.84 | 1137.44
TOTAL NATIONAL LOAD (ACTUAL) | 1163.14 | 1148.24 | 1159.94 | 1149.14 | 1137.44 | 1224.48 | 1335.64 | 1422.34 | 1556.44 | 1710.44 | 1769.34 | 1765.84 | 1631.74 | 1554.24 | 1357.34 | 1482.84 | 1395.24 | 1464.44 | 1464.04 | 1425.84 | 1295.24 | 1220.94 | 1393.14 | 1849.84 | 1781.54 | 1722.94 | 1706.19 | 1727.89 | 1690.29 | 1359.19 | 1223.79 |  | 1849.84 | 1137.44
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
NET IMPORT | 508.6 | 495.8 | 507.2 | 531.4 | 520.5 | 567.04 | 571.7 | 569.7 | 620.5 | 368.3 | 246.5 | 220.3 | 279.9 | 341.2 | 576.5 | 700.7 | 643.9 | 714.3 | 763.6 | 612.4 | 542.7 | 475.3 | 363.1 | 295.7 | 258.2 | 238.4 | 356.2 | 489.4 | 563 | 611.9 | 605.5 |  | 763.6 | 220.3
HZ | 50.076 | 50.069 | 50.026 | 50.043 | 50.062 | 50.056 | 49.948 | 50.062 | 50.031 | 49.995 | 49.973 | 50.014 | 50.047 | 49.851 | 50.054 | 50.01 | 50.06 | 49.84 | 49.95 | 49.99 | 50.05 | 50.07 | 50.04 | 50.04 | 50.03 | 50.062 | 50.012 | 49.947 | 50.018 | 50.13 | 49.945 |  | 50.13 | 49.84
HTD 132KV | 126.1 | 128.2 | 128 | 128 | 129 | 129 | 126.9 | 126.9 | 125.5 | 127.8 | 125.5 | 125.4 | 125.8 | 126.1 | 124.2 | 126.4 | 125.8 | 125.1 | 124.4 | 124.7 | 128.9 | 128.9 | 126.5 | 124.4 | 126.1 | 126.6 | 127.4 | 126.8 | 125.4 | 126.5 | 127.6 |  | 129 | 124.2
SUI 132KV | 130.7 | 132.5 | 131.8 | 131.8 | 132.9 | 132.9 | 130.7 | 130.7 | 128 | 128.8 | 126 | 126.1 | 127.6 | 127.8 | 126.7 | 128.8 | 128.7 | 128.2 | 127.5 | 127.9 | 130.8 | 130.8 | 128.3 | 125.8 | 127.3 | 127.8 | 128.8 | 128.6 | 127.8 | 130.2 | 131.4 |  | 132.9 | 125.8
DUBI 132KV | 128 | 129.6 | 131.7 | 131.7 | 132 | 132 | 126.9 | 126.9 | 127 | 131.6 | 128 | 127.1 | 129.6 | 129.9 | 127.4 | 127.7 | 129..4 | 125.8 | 127.6 | 128.2 | 131.8 | 131.8 | 126.7 | 128 | 129.3 | 130 | 130.6 | 132 | 126.9 | 130 | 128.5 |  | 132 | 125.8
ANAMANI 132KV | 130.4 | 131.4 | 134.1 | 134.1 | 134 | 134 | 128.4 | 128.4 | 129 | 132 | 128 | 126.7 | 129.1 | 129.6 | 127.7 | 129 | 130.2 | 127.4 | 127.4 | 128.8 | 131.7 | 131.7 | 125.9 | 127.4 | 130 | 132.5 | 133.6 | 134.3 | 129 | 132.1 | 131.5 |  | 134.3 | 125.9
KG-A 132KV | 125.4 | 131.4 | 128 | 128 | 131 | 131 | 133 | 133 | 133.6 | 133 | 132.9 | 133.3 | 133.6 | 132 | 131.5 | 136.4 | 135.9 | 135.2 | 135.2 | 134.5 | 136.1 | 136.1 | 135 | 133.7 | 135.7 | 131.2 | 135.5 | 135 | 134 | 135.3 | 133.8 |  | 136.4 | 125.4
KOHALPUR 132KV | 128.5 | 131.2 | 131.8 | 131.8 | 132.9 | 132.9 | 130 | 130 | 126.8 | 130.5 | 131.7 | 132.9 | 134.7 | 135 | 132.2 | 133.3 | 130.5 | 132.2 | 132.2 | 133.1 | 132.2 | 132.2 | 132 | 130.5 | 128.8 | 131.2 | 133.8 | 134.4 | 134.7 | 133.4 | 131.9 |  | 135 | 126.8
SUI 66KV | 65.8 | 66.7 | 66.5 | 66.5 | 66.85 | 66.85 | 65.7 | 65.7 | 64.4 | 65 | 63.6 | 63.5 | 64.2 | 64.3 | 63.7 | 64.5 | 64.8 | 64.5 | 64.5 | 64.5 | 66.1 | 66.1 | 64.7 | 63.4 | 64.3 | 64.3 | 64.9 | 64.7 | 64.3 | 65.5 | 66.1 |  | 66.85 | 63.4
[33 empty] | 0 | 0
Kathmandu Load | 156.028 | 143.014 | 134.559 | 124.44 | 133.34 | 172.54 | 208.54 | 243.84 | 307.74 | 361.48 | 409.14 | 401.58 | 373.26 | 365.18 | 42 | 298.34 | 301.68 | 290.68 | 296.36 | 306.98 | 314.94 | 326.36 | 379.98 | 437.46 | 435.82 | 417.473 | 398.9 | 359.04 | 315.04 | 243.74 | 207.94 |  | 437.46 | 42
MRS-SYU | -1.9 | -1.6 | -4.8 | -12.9 | -9.9 | 1.4 | 5 | 12.2 | 37.2 | 32.6 | 40.9 | 46.4 | 46.6 | 44.7 | 37 | 33.1 | 32.9 | 33.3 | 19.7 | 47.3 | 39.1 | 30.2 | 45.9 | 57 | 56.2 | 53 | 52.9 | 35.8 | 34.5 | 30.4 | 14 | 75 | 57 | -12.9
NMRS-MATA | -4 | -4.5 | -9.2 | -19 | -14.7 | 0.8 | 7.4 | 16.7 | 49.7 | 46.74 | 55.8 | 63.4 | 64.3 | 62.4 | 49 | 42.7 | 42.5 | 44.2 | 22.8 | 62.4 | 54.5 | 43 | 63.2 | 78.7 | 76.8 | 72.4 | 70.8 | 48.6 | 42.9 | 40 | 17.3 | 240 | 78.7 | -19
KL2-MATA | -36 | -38 | -40.5 | -34.4 | -33.8 | -33.4 | -24.8 | -14 | -4.8 | 25 | 40 | 34.2 | 24 | 24.6 | 24.8 | -18.5 | 10.8 | 7.3 | 16.4 | -9.8 | 17 | 33.1 | 34.3 | 43.5 | 43.9 | 34 | 29.5 | 33 | 18 | -15 | -10 | 240 | 43.9 | -40.5
KL1-SYU | -7.2 | -8.7 | -12.8 | -13.2 | -9.4 | -7.4 | -10.2 | -5.2 | 1.5 | 17.4 | 21.8 | 21.8 | 17.9 | 19.4 | 9.3 | 8.2 | 4.3 | 1.9 | 5.6 | 3 | 13.7 | 19.2 | 21.8 | 24.6 | 25.9 | 24.2 | 22.4 | 22 | 10 | -1.3 | -3 | 60 | 25.9 | -13.2
KHIMTI-LAMOSANGHU | 110.888 | 103.874 | 109.719 | 112 | 110 | 120 | 140 | 143 | 133 | 150 | 160 | 141.44 | 119.72 | 108.24 | 123 | 123 | 107.84 | 103.84 | 135.52 | 110.24 | 102.4 | 113.92 | 127.84 | 146.72 | 146.08 | 145.233 | 133.66 | 130 | 120 | 100 | 100 | 120 | 160 | 100
LAMOSHANGU-BHAKTAPUR | 78.4 | 76.7 | 76.6 | 85.9 | 84.2 | 79.5 | 93.4 | 95.7 | 92 | 98.1 | 103.2 | 95.6 | 82.6 | 77 | 81.2 | 82.9 | 78.8 | 76.1 | 91.6 | 78.6 | 76.1 | 82.5 | 87.8 | 97.8 | 97.1 | 96.7 | 90.4 | 98 | 97 | 81 | 80
BALAJU-SYUCHATAR | 55.7 | 59.8 | 64 | 76 | 75.5 | 54.1 | 54.8 | 39.4 | -11.5 | -20.3 | -32 | 39.2 | -37.7 | -38.9 | -16.7 | -7 | -3.8 | -7.5 | 16.5 | -11.6 | -28.5 | -25.3 | -45.5 | -62.5 | -62.1 | -52.3 | -45.8 | -26 | -5 | -5 | 30.6
DHALKE-NAWALPUR I | 93 | 91.8 | 90.8 | 104 | 99.3 | 98.7 | 109.7 | 109.4 | 92 | 91.3 | 84.5 | 75.6 | 62 | 61.6 | 75.2 | 75.7 | 70.3 | 67 | 88.6 | 97.3 | 75 | 68.9 | 66.3 | 70.2 | 70.2 | 75.2 | 81.3 | 92 | 105 | 89.4 | 86.7 |  | 109.7 | 61.6
N. BHARATPUR-BARDGHAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
DAMAK-DUHABI | -4.7 | -4.6 | -4.1 | -3.3 | -4.1 | -9.3 | -15.5 | -22.9 | -36.1 | -40.5 | -45.1 | -46.9 | -36 | -31.1 | -27 | -20.7 | -19.8 | -17 | -20.6 | -25 | -30.2 | -33.6 | -49.7 | -52 | -42.7 | -39.4 | -33.4 | -31 | -21 | -14.7 | -10 |  | -3.3 | -52
HETAUDA-KAMANE | 26.6 | 25.9 | 26.1 | 25.2 | 26.5 | 27.4 | 27.8 | 28.9 | 31.4 | 11.8 | 12 | 11.8 | 11.7 | 10.2 | 13 | 21.4 | 26.1 | 26.1 | 30.2 | 22.1 | 11.8 | 10.1 | 10.3 | 11 | 10.1 | 10 | 9.9 | 9.7 | 9.6 | 26.3 | 26.5 |  | 31.4 | 9.6
MIRCHAIYA LAHAN 2 | 89.8 | 90.8 | 86.1 | 85.3 | 83.6 | 89.7 | 96.2 | 105.5 | 112.4 | 105.6 | 94.3 | 95 | 84.4 | 77.7 | 107.8 | 99 | 103.2 | 107.4 | 108.1 | 95.2 | 95.6 | 80.1 | 106.9 | 111.9 | 106.7 | 105 | 103.8 | 94 | 102 | 102.5 | 105 |  | 112.4 | 77.7
Water Level
UTK | 1984.7 | 1984.92 | 1985.15 | 1985.38 | 1985.62 | 1985.82 |  | 1985.9 |  | 1985.72 |  | 1984.98 | 1984.12 | 1983.72 | 1983.7 | 1983.9 | 1984.12 | 1984.33 | 1984.55 | 1984.75 | 1984.95 | 1985.05 | 1985.05 |  | 1984.43 |  | 1983.64 |  | 1983.43 | 1983.59 | 1983.89
KGA | 522.08 | 522.4 | 522.71 | 523.08 | 523.3 | 523.5 |  | 523.51 |  | 523.36 |  | 523.18 | 522.96 | 522.9 | 522.86 | 522.82 | 522.8 | 522.77 | 522.73 | 522.49 | 522.04 |  | 521.9 |  | 521.46 |  | 520.85 |  | 520.44 | 520.21 | 520.32
MMRS | 623.47 | 623.76 | 624.12 | 624.52 | 624.79 | 625.1 |  | 625.17 |  | 625.06 |  | 624.67 | 624.31 | 623.96 | 623.69 | 623.4 | 623.17 | 622.85 | 623.1 | 623.19 | 623.24 |  | 623.16 |  | 622.49 |  | 621.72 |  | 621.93 | 622.22 | 622.71
MRS | 335.55 | 335.77 | 335.99 | 336.14 | 336.45 | 336.72 |  | 336.9 |  | 336.89 |  | 336.6 | 336.18 | 335.69 | 335.25 | 334.98 | 334.89 | 335.14 | 335.4 | 335.48 | 335.42 |  | 335.48 |  | 335.29 |  | 334.99 |  | 334.7 | 334.55 | 334.56
CHM | 885 | 885.5 | 886 | 886.6 | 887 | 887.3 |  | 886.6 |  | 885.9 |  | 884.7 | 883 | 882.1 | 883.2 | 883.9 | 884.7 | 885.2 | 885.8 | 886.3 | 886.7 |  | 886.6 |  | 885.4 |  | 884 |  | 884 | 885.3 | 885.7
KL 1 | 0: 1518.87; 0.20833: 1518.87; 0.25: 1518.88; 0.33333: 1518.88; 0.83333: 1518.9
Others IPP Detail
Upper Mai Khola(9.98) | 1983.58 | 1983.85 | 1984.12 | 1984.38 | 1984.6 | 1984.8 |  | 1985.02 |  | 1985.22 |  | 1984.98 | 1984.17 | 1983.81 | 1983.8 | 1983.85 | 1983.81 | 1984 | 1984.22 | 1984.55 | 1984.65 |  | 1984.8 |  | 1984.6 |  | 1984.3 |  | 1984.12 | 1984.23 | 1984.45 | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5) | 0.58333: 5087; 0.625: 33470; 0.66667: 211.9583
Upper Hewa Khola Small(8.5) | 0.58333: 2383; 0.625: 1394.5833; 0.66667: 99.2917
Ankhu Khola - 1(8.4) | 0.58333: 1507; 0.66667: 62.7917
Mai sana Cascade(8) | 0.58333: 10990; 0.66667: 457.9167
Upper Naugad Gad(8) | 0.58333: 12850; 0.66667: 535.4167
Taksar Pikhuwa(8) | 0.58333: 2160; 0.66667: 90
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 1983.58 | 1983.85 | 1984.12 | 1984.38 | 1984.6 | 1984.8 | 0 | 1985.02 | 0 | 1985.22 | 0 | 1984.98 | 1984.17 | 1983.81 | 1983.8 | 1983.85 | 1983.81 | 36961 | 36848.8033 | 3441.925 | 1984.65 | 0 | 1984.8 | 0 | 1984.6 | 0 | 1984.3 | 0 | 1984.12 | 1984.23 | 1984.45 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1769.34; 0.041667: 7:30
0
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/0); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/0)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1163.14; 0.66667: 1148.24; 0.70833: 1159.94; 0.72917: 1149.14; 0.75: 1137.44; 0.77083: 1224.48; 0.79167: 1335.64; 0.8125: 1422.34; 0.83333: 1556.44; 0.85417: 1710.44; 0.875: 1769.34; 0.91667: 1765.84; 0.95833: 1631.74 | 1554.24 | 1357.34 | 1482.84 | 1395.24 | 1464.44 | 1464.04 | 1425.84 | 1295.24 | 1220.94 | 1393.14 | 1849.84 | 1781.54 | 1722.94 | 1706.19 | 1727.89 | 1690.29 | 1359.19 | 1223.79
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 1
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/1 |  |  | 2080/10/1 |  |  | Tuesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 598 | 559.6 | 566.1 | 571.9 | 541.1 | 564.8 | 532.9 | 618.1 | 350.9 | 225.5 | 180.3 | 274.7 | 397.4 | 655.8 | 718.9 | 713.1 | 707.9 | 783 | 745.5 | 483 | 525.5 | 379.4 | 384.7 | 310 | 322 | 415.5 | 504.1 | 656.5 | 635.8 | 574.9 | 556
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1791MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1157 | 1157.29 | 1199.29 | 1160.89 | 1167.69 | 1185.19 | 1224.89 | 1342.59 | 1325.69 | 1572.71 | 1507.31 | 1529.89 | 1791.09 | 1589.59 | 1584.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1503.79 | 1462.49 | 1331.69 | 1528.69 | 1707.19 | 1808.99 | 1770.95 | 1743.29 | 1697.99 | 1746.59 | 1542.79 | 1362.29 | 1233.09
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 30.5 | 30.5 | 30.5 | 29.5 | 29 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 27.6 | 25.3 | 26.2 | 26.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 15 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 86 | 30.5 | 15
Likhu-II(55) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 54 | 9.8 | 9.8
Super Dordi (54) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 54 | 10.3 | 10.3
Likhu-IV(52.4) | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 52.4 | 16.4 | 15.3
Upper Marsyangdi "A"(50) | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 50 | 29.1 | 28.3
Upper Bhotekoshi Khola(45) | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 45 | 17.2 | 16.6
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 42 | 8 | 7.5
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 30 | 8.8 | 8.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 7.2 | 7.2
Dordi(27) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 30 | 6.7 | 6.7
Upper Madi(25) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 25 | 8.2 | 8.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 25 | 7.4 | 7.4
Solu Khola(23.5) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 23.5 | 7.2 | 7.2
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 22 | 6.3 | 6.3
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 26.3 | 26.3 | 26.3 | 27.1 | 24.3 | 24.3 | 24.3 | 24.3 | 21.5 | 21.5 | 21.5 | 14.2 | 20 | 22.7 | 23.8 | 27.7 | 19.1 | 16.5 | 16.5 | 19.7 | 17.1 | 17.1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 240 | 27.7 | 14.2
Total IPP | 484.25 | 484.25 | 484.25 | 483.25 | 482.75 | 482.25 | 482.25 | 482.25 | 482.25 | 482.25 | 482.25 | 482.25 | 480.95 | 478.65 | 479.55 | 479.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 468.35 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 1042.4 | 484.25 | 468.35
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 270 | 400 | 420 | 260 | 140 | 15 | 35 | 15 | 20 | 0 | 0 | 15 | 30 | 230 | 300 | 340 | 320 | 230 | 230 | 40 | 0 | 0 | 456 | 420 | 0
Khimti Khola(60) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 30 | 30
Chilime(22.1) | 10 | 10 | 10 | 10 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 22.1 | 10.3 | 10
Total NEA SUBSIDIARIES | 40 | 40 | 40 | 40 | 40.2 | 40.2 | 40.2 | 40.2 | 140.2 | 310.3 | 440.3 | 460.2 | 300.2 | 180.2 | 55.2 | 75.2 | 55.2 | 60.2 | 40.2 | 40.2 | 55.2 | 70.2 | 270.2 | 340.2 | 380.2 | 360.2 | 270.2 | 270.2 | 80.2 | 40.2 | 40.2 | 538.1 | 460.2 | 40
KGA(144) | 0 | 0 | 0 | 0 | 0 | 30 | 96 | 96 | 111.4 | 140 | 133.7 | 144.1 | 60.9 | 60.9 | 30 | 48 | 49 | 49 | 43 | 43 | 62.2 | 62.2 | 98 | 130 | 130 | 134 | 91.1 | 80.1 | 61.1 | 48.7 | 30.6 | 144 | 144.1 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 16 | 35 | 50 | 51.4 | 65 | 65 | 65 | 43 | 43 | 43 | 35 | 35 | 35 | 25 | 25 | 25 | 25 | 69 | 60 | 60 | 45 | 35 | 25 | 25 | 25 | 25 | 70 | 69 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 25 | 34.3 | 34.3 | 68.3 | 55.9 | 69 | 64 | 53.6 | 53.6 | 33.8 | 33.7 | 39.3 | 34 | 34 | 34 | 34 | 34 | 69 | 68 | 68 | 68 | 67.1 | 48.1 | 48.9 | 49.2 | 0 | 69 | 69 | 0
U Trisuli 3A(60) | 38 | 38 | 38 | 39.3 | 39.3 | 39.3 | 39 | 39 | 39.32 | 39.32 | 41.1 | 41.2 | 38.8 | 38.8 | 39.3 | 40.3 | 40.3 | 40.3 | 38.5 | 38.5 | 38.5 | 38.5 | 38.5 | 38 | 38 | 38 | 38 | 38 | 38 | 41.3 | 41.3 | 60 | 41.3 | 38
CHM(30) | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 15 | 23 | 29 | 28.8 | 10 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 15 | 23 | 23 | 28 | 28 | 10 | 0 | 0 | 30 | 29 | 0 | [16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 3.8 | 6 | 11 | 10.1 | 14.6 | 14.6 | 13.6 | 8 | 3.2 | 0.7 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14.6 | 0 | [15 empty] | Tanakpur | 71 | 72 | 70.3 | 75 | 74.1 | 63.3 | 46.9 | 27.8 | 32.8 | 56.6 | 54.8 | 61.7 | 67.4 | 29.2 | 73 | 52.1 | 54.8 | 64.4 | 57 | 54.8 | 64.1 | 67.4 | 61.6 | 68
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [15 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4 | [15 empty] | Muz | 446 | 410 | 423 | 421.3 | 389 | 402 | 181 | 86.3 | 168.8 | 210 | 414 | 435.6 | 416 | 452.7 | 483 | 499 | 375 | 222 | 83 | 190 | 392 | 414.2 | 388.9 | 413
DEVI(14.1) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 10 | 10 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 14.1 | 10.8 | 8.4 | [15 empty] | Ram | 57 | 53.6 | 50.2 | 51.2 | 55 | 43 | 28 | 7 | 7 | 28 | 42 | 49 | 48 | 50.2 | 52 | 37 | 5 | 5 | 5 | 5 | 5 | 50 | 44.5 | 53
MODI(14) | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 14 | 3.6 | 3.6 | [15 empty] | Rax | 24 | 24 | 22.6 | 24.4 | 23 | 24.6 | 24 | 0 | 0 | 30 | 66 | 99 | 108 | 102 | 106 | 88 | 0 | 32 | 107 | 112.6 | 121.6 | 34.2 | 25 | 22
SUN(10.05) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 10.05 | 2.5 | 2.5 | [15 empty] | Sam | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 59.2 | 66.1 | 72.8 | 79 | 73.6 | 73.7 | 73.8 | 69 | 69.4 | 48.2 | 56 | 58 | 53.1 | 73.8 | 70 | 54.9 | 0
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.54 | [16 empty] | 71 | 72 | 70.3 | 75 | 74.1 | 63.3 | 46.9 | 27.8 | 32.8 | 56.6 | 54.8 | 61.7 | 67.4 | 29.2 | 73 | 52.1 | 54.8 | 64.4 | 57 | 54.8 | 64.1 | 67.4 | 61.6 | 68
Total ROR | 77.04 | 77.04 | 77.04 | 78.34 | 90.34 | 161.34 | 255.34 | 270.34 | 326.06 | 363.86 | 381.84 | 388.34 | 253.74 | 248.74 | 197.64 | 223.04 | 229.64 | 223.34 | 199.94 | 195.14 | 211.84 | 201.34 | 325.94 | 352.44 | 362.4 | 349.44 | 300.64 | 260.64 | 224.44 | 205.64 | 138.34 | 489.91 | 388.34 | 77.04 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [16 empty] | 446 | 410 | 423 | 421.3 | 389 | 402 | 181 | 86.3 | 168.8 | 210 | 414 | 435.6 | 416 | 452.7 | 483 | 499 | 375 | 222 | 83 | 190 | 392 | 414.2 | 388.9 | 413
KL2(32) | 0.27083: 4.4 | 32 | 4.4 | 4.4 | [16 empty] | 57 | 53.6 | 50.2 | 51.2 | 55 | 43 | 28 | 7 | 7 | 28 | 42 | 49 | 48 | 50.2 | 52 | 37 | 5 | 5 | 5 | 5 | 5 | 50 | 44.5 | 53
KL3(14) | 0.27083: 1.7 | 14 | 1.7 | 1.7 | [16 empty] | 24 | 24 | 22.6 | 24.4 | 23 | 24.6 | 24 | 0 | 0 | 30 | 66 | 99 | 108 | 102 | 106 | 88 | 0 | 32 | 107 | 112.6 | 121.6 | 34.2 | 25 | 22
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 6.1 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 59.2 | 66.1 | 72.8 | 79 | 73.6 | 73.7 | 73.8 | 69 | 69.4 | 48.2 | 56 | 58 | 53.1 | 73.8 | 70 | 54.9 | 0
TANAKPUR | 68 | 71 | 72 | 70.3 | 75 | 74.1 | 62 | 63.3 | 72 | 46.9 | 32.9 | 27.8 | 32.8 | 56.6 | 54.8 | 61.7 | 67.4 | 29.2 | 73 | 52.1 | 54.8 | 67 | 64.4 | 64.7 | 57 | 52 | 54.8 | 62.5 | 64.1 | 67.4 | 61.6 |  | 75 | 27.8
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 413 | 446 | 410 | 423 | 421.3 | 389 | 432 | 402 | 401 | 181 | 125.6 | 86.3 | 168.8 | 210 | 414 | 435.6 | 416 | 452.7 | 483 | 499 | 375 | 399.6 | 222 | 181 | 83 | 103 | 190 | 253 | 392 | 414.2 | 388.9 |  | 499 | 83
RAMNAGAR | 53 | 57 | 53.6 | 50.2 | 51.2 | 55 | 48 | 43 | 52 | 28 | 6 | 7 | 7 | 28 | 42 | 49 | 48 | 50.2 | 52 | 37 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 44.5 |  | 57 | 5 | [23 empty] | 71 | 0 | 446 | 57 | 24 | 0
RAXAUL 132 | 22 | 24 | 24 | 22.6 | 24.4 | 23 | 22.8 | 24.6 | 26.1 | 24 | 0 | 0 | 0 | 30 | 66 | 99 | 108 | 102 | 106 | 88 | 0 | 0 | 32 | 76 | 107 | 106 | 112.6 | 114.8 | 121.6 | 34.2 | 25 |  | 121.6 | 0 | [23 empty] | 72 | 0 | 410 | 53.6 | 24 | 0
NANPARA(33kV) | [32 empty] | 0 | 0 | [23 empty] | 70.3 | 0 | 423 | 50.2 | 22.6 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test | [20 empty] | 75 | 0 | 421.3 | 51.2 | 24.4 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [23 empty] | 74.1 | 0 | 389 | 55 | 23 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1 | [21 empty] | 63.3 | 0 | 402 | 43 | 24.6 | 0
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2 | [21 empty] | 46.9 | 0 | 181 | 28 | 24 | 71
SAMPATIYA 132 kV | 0 |  |  |  | 0 | 0 | 0 |  | 67 | 71 | 61 | 59.2 | 66.1 | 72.8 | 79 | 73.6 | 73.7 | 73.8 | 69 | 69.4 | 48.2 | 53.9 | 56 | 58 | 58 | 56 | 53.1 | 68.8 | 73.8 | 70 | 54.9 |  | 79 | 0 | [23 empty] | 27.8 | 0 | 86.3 | 7 | 0 | 59.2
Total IMPORT | 556 | 598 | 559.6 | 566.1 | 571.9 | 541.1 | 564.8 | 532.9 | 618.1 | 350.9 | 225.5 | 180.3 | 274.7 | 397.4 | 655.8 | 718.9 | 713.1 | 707.9 | 783 | 745.5 | 483 | 525.5 | 379.4 | 384.7 | 310 | 322 | 415.5 | 504.1 | 656.5 | 635.8 | 574.9 | 0 | 783 | 180.3 | [23 empty] | 32.8 | 0 | 168.8 | 7 | 0 | 66.1
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [23 empty] | 56.6 | 0 | 210 | 28 | 30 | 72.8
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [23 empty] | 54.8 | 0 | 414 | 42 | 66 | 79
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [23 empty] | 61.7 | 0 | 435.6 | 49 | 99 | 73.6
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [23 empty] | 67.4 | 0 | 416 | 48 | 108 | 73.7
TOTAL SYSTEM LOAD (ACTUAL) | 1157.29 | 1199.29 | 1160.89 | 1167.69 | 1185.19 | 1224.89 | 1342.59 | 1325.69 | 1572.71 | 1507.31 | 1529.89 | 1511.09 | 1309.59 | 1304.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1504.79 | 1462.49 | 1231.69 | 1278.69 | 1457.19 | 1558.99 | 1520.95 | 1513.29 | 1467.99 | 1516.59 | 1442.79 | 1363.29 | 1235.09 | 2231.81 | 1572.71 | 1157.29 | [23 empty] | 29.2 | 0 | 452.7 | 50.2 | 102 | 73.8
Interruption/Tripping | 0.33333: 280; 0.375: 280; 0.41667: 280; 0.70833: 100; 0.72917: 250; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 230; 0.83333: 230; 0.85417: 230; 0.875: 100; 0.91667: 0; 0.95833: 0 |  | 280 | 0 | [23 empty] | 73 | 0 | 483 | 52 | 106 | 69
TOTAL SYSTEM LOAD (EXPECTED) | 1157.29 | 1199.29 | 1160.89 | 1167.69 | 1185.19 | 1224.89 | 1342.59 | 1325.69 | 1572.71 | 1507.31 | 1529.89 | 1791.09 | 1589.59 | 1584.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1504.79 | 1462.49 | 1331.69 | 1528.69 | 1707.19 | 1808.99 | 1770.95 | 1743.29 | 1697.99 | 1746.59 | 1542.79 | 1363.29 | 1235.09 | 1693.71 | 1808.99 | 1157.29 | [23 empty] | 52.1 | 0 | 499 | 37 | 88 | 69.4
TOTAL NATIONAL LOAD (ACTUAL) | 1157.29 | 1199.29 | 1160.89 | 1167.69 | 1185.19 | 1224.89 | 1342.59 | 1325.69 | 1572.71 | 1507.31 | 1529.89 | 1791.09 | 1589.59 | 1584.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1503.79 | 1462.49 | 1331.69 | 1528.69 | 1707.19 | 1808.99 | 1770.95 | 1743.29 | 1697.99 | 1746.59 | 1542.79 | 1362.29 | 1233.09 |  | 1808.99 | 1157.29 | [23 empty] | 54.8 | 0 | 375 | 5 | 0 | 48.2
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 64.4 | 0 | 222 | 5 | 32 | 56
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 57 | 0 | 83 | 5 | 107 | 58
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 54.8 | 0 | 190 | 5 | 112.6 | 53.1
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 64.1 | 0 | 392 | 5 | 121.6 | 73.8
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 67.4 | 0 | 414.2 | 50 | 34.2 | 70
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 0 | [23 empty] | 61.6 | 0 | 388.9 | 44.5 | 25 | 54.9
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 0 | [23 empty] | 68 | 0 | 413 | 53 | 22 | 0
NET IMPORT | 556 | 598 | 559.6 | 566.1 | 571.9 | 541.1 | 564.8 | 532.9 | 618.1 | 350.9 | 225.5 | 180.3 | 274.7 | 397.4 | 655.8 | 718.9 | 713.1 | 707.9 | 782 | 745.5 | 483 | 525.5 | 379.4 | 384.7 | 310 | 322 | 415.5 | 504.1 | 656.5 | 634.8 | 572.9 |  | 782 | 180.3
HZ | 50.011 | 49.864 | 49.976 | 49.982 | 49.977 | 50.038 | 50.032 | 50.024 | 49.86 | 50.006 | 50.028 | 50.118 | 50.027 | 50.037 | 50.032 | 50.029 | 50.033 | 50.02 | 49.89 | 49.779 | 50.199 | 50.095 | 49.939 | 50.035 | 50.021 | 50.021 | 50.07 | 50.07 | 50.07 | 49.99 | 50.02 |  | 50.199 | 49.779
HTD 132KV | 127.5 | 125.8 | 128 | 127.2 | 127.1 | 128.9 | 126.6 | 126.3 | 126.2 | 126.9 | 123.4 | 125 | 125.4 | 127.5 | 125.3 | 125.1 | 125.1 | 123.8 | 124 | 124.2 | 127.7 | 126.8 | 127.4 | 126.2 | 128 | 128 | 129.9 | 129.9 | 126.6 | 127.4 | 127.4 |  | 129.9 | 123.4
SUI 132KV | 131.8 | 130.4 | 132.3 | 131.2 | 131.6 | 132.4 | 130.6 | 129.8 | 128.2 | 128.3 | 125.1 | 126.5 | 127.2 | 129 | 127.5 | 128 | 127.8 | 127.5 | 127 | 126.9 | 129.9 | 129.2 | 128.8 | 127.1 | 129 | 129 | 132 | 132 | 128.6 | 130.6 | 130.6 |  | 132.4 | 125.1
DUBI 132KV | 129.1 | 129.3 | 132.3 | 128.9 | 128.3 | 129 | 125.6 | 128.7 | 128.7 | 131.5 | 123.3 | 130.9 | 129.2 | 131.4 | 124.1 | 126 | 124.7 | 124.2 | 128 | 125.3 | 128.5 | 128 | 126.1 | 130.2 | 130.4 | 130.4 | 130.7 | 130.7 | 128.4 | 128.3 | 128.3 |  | 132.3 | 123.3
ANAMANI 132KV | 132.6 | 132.9 | 135 | 133.6 | 133.5 | 133.3 | 129.5 | 130.6 | 130 | 132.4 | 123.8 | 131.3 | 129.6 | 132.1 | 125.7 | 128.3 | 127 | 127.1 | 130 | 126.8 | 130.1 | 128.9 | 124.9 | 129.2 | 131.2 | 131.2 | 132.5 | 132.5 | 131.9 | 131.7 | 131.7 |  | 135 | 123.8
KG-A 132KV | 131.1 | 130.5 | 131.8 | 131.4 | 132.6 | 133.1 | 135.9 | 135.2 | 135.5 | 132.36 | 132.5 | 133 | 132.6 | 132.4 | 130.6 | 133.3 | 133 | 132.7 | 131.5 | 132.5 | 135.8 | 135.2 | 135 | 135.3 | 134 | 134 | 136.4 | 136.4 | 133.3 | 134 | 134 |  | 136.4 | 130.5
KOHALPUR 132KV | 131.4 | 129.1 | 129.6 | 129.8 | 132.5 | 128.6 | 132.1 | 129.1 | 126.7 | 128.9 | 131 | 131 | 129.8 | 134.8 | 134 | 135.4 | 124 | 124.4 | 131 | 135 | 126.9 | 127.5 | 128 | 128.5 | 132.4 | 132.4 | 128.4 | 128.4 | 132.1 | 125.7 | 125.7 |  | 135.4 | 124
SUI 66KV | 66.2 | 66 | 66.7 | 66 | 66.4 | 66.9 | 65.8 | 65.3 | 64.3 | 64.7 | 63.1 | 63.8 | 64.1 | 65 | 64.1 | 64.5 | 64.5 | 64.2 | 64 | 63.8 | 65.7 | 65.3 | 65.1 | 63.7 | 64.7 | 64.7 | 66 | 66 | 64.2 | 65.7 | 65.7 |  | 66.9 | 63.1
[33 empty] | 0 | 0
Kathmandu Load | 148.24 | 137.64 | 156.64 | 130.048 | 131.796 | 168.692 | 211.712 | 244.664 | 333.12 | 350.608 | 391.128 | 391.9 | 367.335 | 360.66 | 42 | 322.5 | 310.96 | 304.24 | 264.44 | 322.94 | 326.4 | 339.74 | 396.1 | 438.96 | 430.2 | 427.04 | 384.88 | 384.88 | 333.12 | 257.94 | 178.74 |  | 438.96 | 42
MRS-SYU | -3.8 | -10 | -10 | -10.8 | -8.4 | 9.5 | 16.5 | 29.1 | 40.5 | 39.3 | 31.1 | 46.2 | 28.5 | 30.3 | 27.5 | 26.7 | 27.1 | 25.5 | 25.5 | 23.2 | 29.4 | 28 | 44.2 | 47 | 47 | 47 | 38.9 | 38.9 | 26.7 | 33.6 | 13 | 75 | 47 | -10.8
NMRS-MATA | -6.6 | -16 | -15 | -14.8 | -11.5 | 13 | 20.7 | 39 | 55.6 | 55.3 | 42.1 | 64.9 | 38.8 | 42.9 | 36.4 | 33.6 | 34.1 | 31.9 | 21.4 | 28 | 41.4 | 39 | 61 | 63.2 | 64 | 64 | 52.1 | 52.1 | 31.5 | 43 | 19.1 | 240 | 64.9 | -16
KL2-MATA | -30 | -32 | -34 | -41.9 | -38 | -32 | -23.2 | -21.8 | 2.9 | 17.5 | 26.6 | 24 | 28 | 35 | 23 | 13.1 | 11 | 10.6 | 20 | 27 | 28 | 32 | 43 | 53 | 50 | 50 | 43.1 | 43.1 | 35 | -12 | -30.8 | 240 | 53 | -41.9
KL1-SYU | -11 | -14 | -14 | -15.9 | -12.6 | -5.9 | -7.4 | -5.6 | 7.9 | 17.7 | 18.6 | 20 | 17.3 | 20.7 | 8.4 | 2.4 | 1.9 | 1.9 | 1 | 5 | 16.6 | 18.4 | 24 | 30 | 30 | 30 | 18.9 | 18.9 | 12.2 | 2.8 | -3.5 | 60 | 30 | -15.9
KHIMTI-LAMOSANGHU | 110 | 120 | 140 | 122.508 | 111.356 | 93.152 | 114.472 | 113.324 | 133.66 | 128.248 | 174.988 | 137.76 | 155.895 | 127.92 | 139.4 | 137.76 | 127.92 | 126.4 | 96 | 144 | 117.76 | 129.6 | 131.36 | 150.56 | 144 | 144 | 139.84 | 139.84 | 135.68 | 95.2 | 85.6 | 120 | 174.988 | 85.6
LAMOSHANGU-BHAKTAPUR | 80 | 77 | 83.7 | 86.8 | 80.8 | 72 | 81.4 | 80.4 | 90.4 | 88.5 | 107.2 | 91.9 | 99.8 | 86.2 | 92 | 92.4 | 89 | 90 | 94 | 98 | 85 | 91 | 91 | 100 | 97 | 97 | 94 | 94 | 92.3 | 72.5 | 67.4 |  | 107.2 | 67.4
BALAJU-SYUCHATAR | 59 | 73..6 | 75.6 | 25.4 | 70.9 | 39.7 | 30.1 | 12.7 | -17.1 | -30.2 | -11.7 | -38.7 | -5.8 | -21.4 | 0.8 | 5.9 | 9.6 | 12.4 | 18 | 8 | -19 | -15.3 | -46 | -42 | -40 | -40 | -28.4 | -28.4 | 3 | 8.7 | 39.5 |  | 75.6 | -46
DHALKE-NAWALPUR I | 92 | 99.5 | 98 | 106.8 | 93.6 | 89.3 | 91.4 | 86.2 | 85.8 | 74.9 | 95.3 | 72.6 | 91.4 | 67.4 | 85 | 85.1 | 81.3 | 89 | 92 | 94 | 75 | 79 | 64 | 71 | 64.3 | 64.3 | 66.1 | 66.1 | 78 | 82 | 75.2 |  | 106.8 | 64
N. BHARATPUR-BARDGHAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6 | -6 | 0 | 0 | 4.3 | -4.9 | -1.6 |  | 4.3 | -6
DAMAK-DUHABI | -5.2 | -4 | -4 | 0.9 | -5.2 | -11.3 | -16.1 | -21.9 | -39 | -40.7 | -43.3 | -34.4 | -30.5 | -24.6 | -16.2 | -13.9 | -18.9 | -19.3 | -14 | -22 | -31 | -40 | -60 | -59 | -47 | -47 | -37.2 | -37.2 | -22.2 | -17 | -12.9 |  | 0.9 | -60
HETAUDA-KAMANE | 26 | 24 | 21 | 26 | 25.6 | 27.7 | 28.6 | 29.3 | 13.8 | 11.7 | 12.6 | 12.5 | 12.8 | 12.6 | 16 | 25.1 | 25.5 | 26 | 26 | 15 | 12 | 12 | 12 | 12 | 11 | 11 | 10.1 | 10.1 | 16.2 | 16.2 | 23.3 |  | 29.3 | 10.1
MIRCHAIYA LAHAN 2 | 95 | 95 | 87 | 94.5 | 91.8 | 97.9 | 101.7 | 105.3 | 109.9 | 96.4 | 99.9 | 84.9 | 78.3 | 69 | 103.2 | 111.9 | 108.7 | 116 | 105 | 113 | 89 | 98 | 123 | 105 | 94.3 | 94.3 | 98.7 | 98.7 | 104.6 | 105.8 | 99.2 |  | 123 | 69
Water Level
UTK | 1984.1 | 1984.4 | 1984.61 | 1984.85 | 1985.08 | 1985.32 |  | 1985.5 |  | 1985.4 |  | 1984.6 | 1983.7 | 1983.38 | 1983.35 | 1983.5 | 1983.68 | 1983.82 | 1983.9 | 1984.22 | 1984.6 | 1984.52 | 1984.58 |  | 1983.9 | 1983.48 | 1982.95 |  | 1982.91 | 1983.11
KGA | 520.7 | 521.08 | 521.4 | 521.73 | 522.07 | 522.37 |  | 522.3 |  | 521.94 |  | 521.49 | 521.08 | 521.14 | 521.26 | 521.32 | 521.37 | 521.42 | 521.5 | 521.57 | 521.56 | 521.56 | 521.53 |  | 521.12 |  | 520.64 |  | 520.46 | 520.52
MMRS | 623.88 | 623.92 | 623.96 | 624.18 | 624.63 | 624.86 |  | 624.86 |  | 624.59 |  | 624.17 | 623.72 | 623.56 | 623.21 | 622.91 | 622.84 | 622.79 | 622.7 | 622.8 | 622.82 | 622.86 | 622.7 |  | 622.2 |  | 621.7 |  | 621.6 | 621.5 | 621.57
MRS | 335.15 | 335.78 | 336.16 | 336.49 | 336.67 | 336.86 |  | 336.81 |  | 336.5 |  | 336.11 | 335.61 | 335.2 | 334.93 | 334.67 | 334.79 | 335.07 | 335.26 | 335.42 | 335.55 | 335.63 | 335.65 |  | 335.33 |  | 334.92 |  | 334.54 | 334.17
CHM | 886.3 | 886.5 | 886.9 | 887.3 | 887.4 | 887.2 |  | 887 |  | 886.6 |  | 885.7 | 884.5 | 884.9 | 885.4 | 885.9 | 885.8 | 885.7 | 885.5 | 885.4 | 885.2 | 885.3 | 885.5 |  | 885 |  | 883.5 |  | 882
KL 1 | 0: 1518.91
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1791.09; 0.041667: 8:00
1
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/1); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/1)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1157.29; 0.66667: 1199.29; 0.70833: 1160.89; 0.72917: 1167.69; 0.75: 1185.19; 0.77083: 1224.89; 0.79167: 1342.59; 0.8125: 1325.69; 0.83333: 1572.71; 0.85417: 1507.31; 0.875: 1529.89; 0.91667: 1791.09; 0.95833: 1589.59 | 1584.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1504.79 | 1462.49 | 1331.69 | 1528.69 | 1707.19 | 1808.99 | 1770.95 | 1743.29 | 1697.99 | 1746.59 | 1542.79 | 1363.29 | 1235.09
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 2
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/2 |  |  | 2080/10/2 |  |  | Wednesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 590.1 | 546.7 | 547.3 | 566.3 | 624.9 | 609.2 | 635 | 595.3 | 480 | 435.4 | 350.5 | 476.9 | 540.9 | 519.5 | 724.8 | 721.4 | 722.5 | 813.5 | 720 | 572.7 | 584.6 | 587.5 | 618.1 | 537.8 | 552.4 | 539.3 | 563.8 | 588.3 | 678.1 | 663.1 | 555.6
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1796MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1150 | 1190.79 | 1194.69 | 1151.29 | 1149.89 | 1168.69 | 1266.59 | 1340.39 | 1433.79 | 1588.89 | 1719.89 | 1795.79 | 1717.59 | 1704.09 | 1650.79 | 1577.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1503.59 | 1307.49 | 1513.99 | 1672.89 | 1847.19 | 1803.85 | 1728.09 | 1683.59 | 1649.79 | 1353.99 | 1355.69 | 1268.99
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28 | 28 | 28 | 28 | 28.4 | 29.1 | 29.1 | 29.1 | 29.8 | 86 | 29.8 | 28
Likhu-II(55) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 54 | 9.8 | 9.8
Super Dordi (54) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 54 | 10.3 | 10.3
Likhu-IV(52.4) | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 16.5 | 16.5 | 52.4 | 16.5 | 15.3
Upper Marsyangdi "A"(50) | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 50 | 29.1 | 29.1
Upper Bhotekoshi Khola(45) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 17.3 | 17.3 | 45 | 17.3 | 16.6
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14
Mistri Khola(42) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 42 | 8 | 7
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 8.8 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 8.7 | 8.7 | 28 | 8.7 | 7.2
Dordi(27) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6.4 | 6.4 | 30 | 7 | 6.4
Upper Madi(25) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 6.5 | 6.5 | 25 | 8.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.2 | 7.2 | 25 | 7.4 | 7.2
Solu Khola(23.5) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.6 | 7.6 | 23.5 | 7.6 | 7.2
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 10.4 | 10.4 | 22 | 10.4 | 6.3
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 15 | 15 | 15 | 23.8 | 23.7 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 23.6 | 23.6 | 23 | 21 | 18.7 | 18.7 | 17 | 13.7 | 21.8 | 20.9 | 21.1 | 22 | 22.5 | 240 | 23.8 | 13.7
Total IPP | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 481.65 | 479.95 | 479.95 | 479.95 | 479.95 | 480.35 | 481.05 | 481.05 | 486.15 | 486.85 | 1042.4 | 486.85 | 479.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 150 | 250 | 210 | 230 | 140 | 70 | 76 | 76 | 76 | 36 | 30 | 30 | 15 | 60 | 100 | 150 | 150 | 160 | 150 | 105 | 70 | 30 | 0 | 456 | 250 | 0
Khimti Khola(60) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 30 | 30
Chilime(22.1) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 22.1 | 10.2 | 10.2
Total NEA SUBSIDIARIES | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 55.2 | 80.2 | 190.2 | 290.2 | 250.2 | 270.2 | 180.2 | 110.2 | 116.2 | 116.2 | 116.2 | 76.2 | 70.2 | 70.2 | 55.2 | 100.2 | 140.2 | 190.2 | 190.2 | 200.2 | 190.2 | 145.2 | 110.2 | 70.2 | 40.2 | 538.1 | 290.2 | 40.2
KGA(144) | 30.6 | 0 | 0 | 0 | 0 | 30.6 | 70 | 70.7 | 100 | 112 | 111.9 | 111.4 | 81.5 | 80.8 | 97.6 | 97 | 97 | 97.7 | 86.2 | 86.2 | 60.8 | 60.8 | 60.8 | 60.8 | 71 | 61 | 60.7 | 60.5 | 30.5 | 0 | 0 | 144 | 112 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 60 | 60 | 60 | 60 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 25 | 25 | 50 | 65 | 65 | 35 | 25 | 25 | 25 | 0 | 0 | 70 | 65 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 45.5 | 68 | 52.6 | 60.5 | 61.2 | 61.2 | 57.5 | 44.4 | 20.7 | 21.9 | 22 | 22 | 22 | 16.6 | 16.6 | 49.5 | 67.2 | 57 | 44 | 33 | 33 | 32.4 | 32.4 | 0 | 69 | 68 | 0
U Trisuli 3A(60) | 41.3 | 41.3 | 41.3 | 39.3 | 39.1 | 37.8 | 37.3 | 37.3 | 37.3 | 37 | 39.1 | 39.1 | 39.1 | 39.8 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 37 | 37.3 | 39.1 | 39.1 | 60 | 41.3 | 37
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 15 | 15 | 15 | 23 | 23 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 10 | 23 | 28 | 28 | 27.5 | 15 | 10 | 10 | 0 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 1.3 | 1.3 | 5.7 | 5.3 | 5.3 | 5.3 | 3 | 5.5 | 2 | 0.6 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 5.7 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 9.3 | 9.3 | 14.1 | 10.8 | 8.9
MODI(14) | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.4 | 3.4 | 14 | 3.6 | 3.3
SUN(10.05) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 10.05 | 2.5 | 2.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.54
Total ROR | 113.34 | 82.74 | 82.74 | 80.74 | 80.54 | 119.84 | 194.34 | 236.94 | 321.74 | 318.04 | 328.54 | 335.24 | 305.34 | 258.04 | 259.84 | 235.54 | 246.74 | 245.24 | 236.24 | 232.74 | 180.54 | 180.14 | 247.84 | 293.54 | 300.5 | 245.54 | 223.74 | 209.74 | 174.44 | 121.24 | 78.84 | 489.91 | 335.24 | 78.84
KL1(60) | 0.66667: 20; 0.70833: 11.4; 0.72917: 11.4; 0.75: 11.4; 0.77083: 10.9; 0.79167: 10.9; 0.8125: 0 | 60 | 20 | 0
KL2(32) | 0.66667: 10; 0.70833: 4.4; 0.72917: 4.4; 0.75: 4.4; 0.77083: 3.3; 0.79167: 3.3; 0.8125: 0 | 32 | 10 | 0
KL3(14) | 0.66667: 3; 0.70833: 1.6; 0.72917: 1.6; 0.75: 1.6; 0.77083: 1.2; 0.79167: 1.2; 0.8125: 0 | 14 | 3 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 17.4 | 17.4 | 15.4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 17.4 | 0
TANAKPUR | 64.5 | 71.3 | 69 | 70.7 | 69.3 | 72.7 | 64 | 71.1 | 66.3 | 62.6 | 64.8 | 47.6 | 50.6 | 61.9 | 61.5 | 71 | 71.6 | 68.5 | 68.7 | 62 | 54.7 | 63.6 | 60.3 | 66 | 72.8 | 60.4 | 55.7 | 64 | 62 | 64.3 | 69.2 |  | 72.8 | 47.6
KATAIYA | 0.33333: 0; 0.375: 0; 0.41667: 0; 0.45833: 0; 0.5: 0; 0.54167: 0; 0.58333: 0; 0.625: 0; 0.66667: 0; 0.70833: 0; 0.72917: 0; 0.75: 0; 0.77083: 0; 0.79167: 0; 0.8125: 0; 0.91667: 0; 0.95833: 0 |  | 0 | 0
MUJAFFARPUR | 426.2 | 442.8 | 404.3 | 405.6 | 419.6 | 429.2 | 440.2 | 455.5 | 361 | 243.1 | 262 | 200 | 287.8 | 362 | 333 | 413 | 407 | 420 | 486 | 430 | 381 | 386 | 369 | 388 | 335 | 372 | 361.6 | 378.2 | 398.7 | 392.8 | 407.4 |  | 486 | 200
RAMNAGAR | 41.7 | 52 | 49.4 | 52 | 57 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 29.6 | 28.6 | 35 | 57 | 60 | 62 | 60 | 53 | 30 | 30 | 35 | 35 | 30 | 25 | 26.8 | 25.9 | 25 | 21.5 | 20.3 |  | 62 | 5
RAXAUL 132 | 23.2 | 24 | 24 | 19 | 20.4 | 118 | 100 | 103.4 | 83 | 97.6 | 39 | 40 | 38 | 16.3 | 16 | 110 | 109 | 94 | 126 | 110 | 60 | 56 | 74 | 74 | 44 | 42 | 42 | 41.6 | 42.6 | 138 | 100.5 |  | 138 | 16
NANPARA(33kV) | 0.5: 0; 0.54167: 0 |  | 0 | 0
BISHANPUR(33kV) | 0.5: 0; 0.54167: 0 |  | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | 0.5: 0; 0.54167: 0 |  | 0 | 0
RAJBIRAJ(33kV) | 0.5: 0; 0.54167: 0 |  | 0 | 0 |  | Line1
RAXAUL(33kV) | 0.5: 0; 0.54167: 0 |  | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 0 | 0 | 0 |  | 0 | 0 |  |  | 80 | 71.7 | 64.6 | 57.9 | 70.9 | 72.1 | 74 | 73.8 | 73.8 | 78 | 72.8 | 65 | 47 | 49 | 49.2 | 55.1 | 56 | 53 | 53.2 | 54.1 | 60 | 61.5 | 65.7 |  | 80 | 0
Total IMPORT | 555.6 | 590.1 | 546.7 | 547.3 | 566.3 | 624.9 | 609.2 | 635 | 595.3 | 480 | 435.4 | 350.5 | 476.9 | 540.9 | 519.5 | 724.8 | 721.4 | 722.5 | 813.5 | 720 | 572.7 | 584.6 | 587.5 | 618.1 | 537.8 | 552.4 | 539.3 | 563.8 | 588.3 | 678.1 | 663.1 | 0 | 813.5 | 350.5
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1190.79 | 1194.69 | 1151.29 | 1149.89 | 1168.69 | 1266.59 | 1340.39 | 1433.79 | 1588.89 | 1569.89 | 1495.79 | 1437.59 | 1444.09 | 1390.79 | 1377.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1504.59 | 1307.49 | 1363.99 | 1472.89 | 1597.19 | 1523.85 | 1478.09 | 1433.59 | 1399.79 | 1353.99 | 1355.69 | 1268.99 | 2231.81 | 1601.59 | 1149.89
Interruption/Tripping | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 280 | 260 | 260 | 200 | [6 empty] | 150 | 200 | 250 | 280 | 250 | 250 | 250 |  |  |  |  | 300 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1190.79 | 1194.69 | 1151.29 | 1149.89 | 1168.69 | 1266.59 | 1340.39 | 1433.79 | 1588.89 | 1719.89 | 1795.79 | 1717.59 | 1704.09 | 1650.79 | 1577.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1504.59 | 1307.49 | 1513.99 | 1672.89 | 1847.19 | 1803.85 | 1728.09 | 1683.59 | 1649.79 | 1353.99 | 1355.69 | 1268.99 | 1693.71 | 1847.19 | 1149.89
TOTAL NATIONAL LOAD (ACTUAL) | 1190.79 | 1194.69 | 1151.29 | 1149.89 | 1168.69 | 1266.59 | 1340.39 | 1433.79 | 1588.89 | 1719.89 | 1795.79 | 1717.59 | 1704.09 | 1650.79 | 1577.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1503.59 | 1307.49 | 1513.99 | 1672.89 | 1847.19 | 1803.85 | 1728.09 | 1683.59 | 1649.79 | 1353.99 | 1355.69 | 1268.99 |  | 1847.19 | 1149.89
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
NET IMPORT | 555.6 | 590.1 | 546.7 | 547.3 | 566.3 | 624.9 | 609.2 | 635 | 595.3 | 480 | 435.4 | 350.5 | 476.9 | 540.9 | 519.5 | 724.8 | 721.4 | 722.5 | 813.5 | 719 | 572.7 | 584.6 | 587.5 | 618.1 | 537.8 | 552.4 | 539.3 | 563.8 | 588.3 | 678.1 | 663.1 |  | 813.5 | 350.5
HZ | 50.03 | 49.97 | 49.94 | 49.948 | 49.945 | 50.011 | 49.967 | 49.827 | 50.043 | 50.109 | 49.961 | 50.06 | 50.075 | 49.982 | 50.031 | 50.093 | 49.976 | 50.04 | 49.959 | 49.959 | 50.053 | 50.1 | 49.99 | 50.042 | 49.964 | 50.026 | 50.057 | 50.017 | 50.02 | 49.99 | 50.05 |  | 50.109 | 49.827
HTD 132KV | 127.8 | 127 | 127 | 128.3 | 127.8 | 127.4 | 126.8 | 125.3 | 125.4 | 127.7 | 126.1 | 125.8 | 128.7 | 124.6 | 128.8 | 121.9 | 122.9 | 122.4 | 121.1 | 121.1 | 128.3 | 127.3 | 127.9 | 127.3 | 127.8 | 129.5 | 129 | 130.3 | 128.36 | 128.5 | 128.6 |  | 130.3 | 121.1
SUI 132KV | 131.9 | 131.2 | 131.2 | 132.4 | 132.2 | 131.3 | 130.2 | 128.7 | 128.5 | 128.9 | 128 | 127.6 | 130.6 | 125.7 | 130.5 | 124.3 | 125.9 | 125.3 | 124 | 124 | 129.5 | 128.9 | 130 | 129.3 | 129.4 | 131.4 | 131.1 | 132.2 | 130.5 | 130.7 | 132.1 |  | 132.4 | 124
DUBI 132KV | 127.7 | 129.4 | 129.4 | 127.5 | 127.4 | 128.8 | 125.7 | 127.5 | 124.9 | 127.3 | 128.4 | 128 | 128 | 128.3 | 126.5 | 126.3 | 127.9 | 124 | 126.5 | 126.5 | 130.8 | 128.5 | 128.5 | 127.3 | 128.5 | 128.3 | 128.2 | 126.8 | 130 | 126.9 | 129.6 |  | 130.8 | 124
ANAMANI 132KV | 129.9 | 132.4 | 132.4 | 130.2 | 130.6 | 130 | 125.9 | 128.4 | 127 | 128.6 | 127.9 | 127.4 | 127.4 | 128.2 | 127.8 | 128.2 | 131.2 | 126.4 | 128 | 128 | 131.4 | 129.5 | 128.4 | 127.4 | 129.4 | 129.6 | 130.9 | 129.7 | 132.9 | 129.9 | 132.1 |  | 132.9 | 125.9
KG-A 132KV | 134.4 | 131.4 | 131.4 | 130.9 | 131.7 | 130.3 | 133.4 | 131.6 | 134.8 | 134.6 | 133.8 | 132.9 | 132.6 | 130.2 | 132.3 | 131.3 | 131.8 | 132.4 | 132.8 | 132.8 | 133.7 | 133.4 | 133.3 | 132.6 | 133.1 | 134.9 | 135.3 | 136.1 | 134.2 | 131.8 | 134.2 |  | 136.1 | 130.2
KOHALPUR 132KV | 125.4 | 124.6 | 124.6 | 126.2 | 135.5 | 126.8 | 134.6 | 126.2 | 133.5 | 134 | 131.1 | 130.3 | 135.3 | 126.4 | 133.2 | 127.2 | 129.6 | 130 | 129.1 | 129.1 | 132.3 | 130.5 | 128 | 132.5 | 136.4 | 132.4 | 134.7 | 135.6 | 134.4 | 133.4 | 130.6 |  | 136.4 | 124.6
SUI 66KV | 66.2 | 66.2 | 66.2 | 66.7 | 66.5 | 66.2 | 65.8 | 64.7 | 64.9 | 65 | 64 | 63.8 | 65.4 | 63 | 65.4 | 62.5 | 63.1 | 63.2 | 62.5 | 62.5 | 65.1 | 64.8 | 65.2 | 64.9 | 64.7 | 66 | 65.5 | 66.2 | 65.3 | 65.6 | 66.5 |  | 66.7 | 62.5
[33 empty] | 0 | 0
Kathmandu Load | 156.36 | 148.88 | 135.3 | 132.417 | 136.77 | 172.099 | 208.309 | 240.91 | 309.398 | 361.811 | 404.948 | 424.156 | 407.401 | 439.14 | 42 | 397.704 | 388.334 | 372.44 | 371.14 | 367.64 | 358.14 | 366.54 | 393.74 | 445.5 | 443.5 | 416.74 | 399.26 | 386.16 |  | 265.08 | 191.66 |  | 445.5 | 42
MRS-SYU | -0.6 | -5.7 | -10.3 | -9.1 | -8.1 | -15 | 2.3 | 4 | 29.2 | 28.6 | 35.4 | 36.4 | 44.3 | 40.9 | 44 | 37.2 | 36.2 | 36 | 31.8 | 31.8 | 27.2 | 26.3 | 34.3 | 40.1 | 37.9 | 32.7 | 28.9 | 31.2 | 29.8 | 7.6 | -2.4 | 75 | 44.3 | -15
NMRS-MATA | -1.2 | -7.3 | -13.8 | -12.9 | -10.2 | -20.4 | 1.4 | 3.4 | 39.6 | 39.8 | 47.6 | 48.9 | 61.4 | 54.6 | 61.2 | 48 | 46.9 | 47 | 40.2 | 40.2 | 38.9 | 36.2 | 45 | 53.1 | 49.3 | 43.7 | 38.5 | 42.8 | 35.2 | 5.9 | -5.4 | 240 | 61.4 | -20.4
KL2-MATA | -38.4 | -37.9 | -36 | -36 | -40.1 | -8.2 | -5.7 | -0.5 | 7.3 | 34.2 | 52.9 | 60 | 24 | 51.7 | 25 | 40 | 35.6 | 31 | 34 | 34 | 47 | 50 | 78 | 79 | 82 | 65 | 63 | 54.4 | 61.9 | 21.6 | -4.3 | 240 | 82 | -40.1
KL1-SYU | -9.5 | -9.8 | -9.7 | -13.6 | -13.7 | -5.4 | -5.4 | -2.4 | 0.8 | 18.7 | 26 | 28 | 21 | 24.3 | 23.3 | 11.1 | 9.9 | 5 | 6 | 6 | 29.2 | 29 | 35 | 37 | 38 | 29.1 | 26.9 | 25.3 | 16.2 | 6.7 | -2.4 | 60 | 38 | -13.7
KHIMTI-LAMOSANGHU | 110.72 | 114.24 | 109.76 | 110.677 | 115.73 | 129.259 | 124.369 | 145.07 | 141.158 | 149.471 | 149.308 | 158.316 | 164.161 | 170 | 149.966 | 165.664 | 163.994 | 160 | 163.2 | 163.2 | 124.8 | 134.4 | 112 | 142.4 | 142.4 | 156.8 | 152.52 | 144.32 | 119.72 | 132.64 | 115.52 | 120 | 170 | 109.76
LAMOSHANGU-BHAKTAPUR | 81.4 | 82.5 | 78.8 | 80.8 | 82.2 | 88.8 | 86.1 | 95.9 | 94.6 | 99.3 | 98.6 | 100.9 | 103.4 | 96.8 | 96.7 | 104.3 | 102.9 | 98 | 106.4 | 106.4 | 88 | 93.1 | 81 | 95.4 | 96 | 102.4 | 98.7 | 95 | 83.5 | 92.1 | 83.3
BALAJU-SYUCHATAR | 77.3 | 28 | 21.4 | 73 | 71.7 | 68 | 44.8 | 43.4 | 0.5 | -16.9 | -30.2 | -31.6 | -26.4 | -38.3 | -27.3 | -9.9 | -7.7 | 8 | -1.7 | -1.7 | -16.3 | -14 | -51.4 | -55.3 | -55 | -30 | -27.5 | -27 | -26.9 | 35.8 | 57.9
DHALKE-NAWALPUR I | 75.2 | 102 | 93.5 | 91.1 | 98.4 | 85.6 | 84.7 | 91.5 | 84.2 | 80.7 | 96.7 | 96 | 50.7 | 76.2 | 71.4 | 94.6 | 95 | 90 | 104.1 | 104.1 | 77 | 75.3 | 89.3 | 100 | 102 | 98 | 87 | 72.5 | 91.5 | 79.6 | 76.7 |  | 104.1 | 50.7
N. BHARATPUR-BARDGHAT I | 7.7 | 19.1 | 23.2 | 22.1 | 19.2 | 32 | 28.7 | 31.5 | 8.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | -13.4 | -13.3 | -15 | -8.1 | -8.1 | -6 | -5.1 | -3.7 | 1 | 0 | -1.3 | -2.6 | -3.8 | 2.1 | 15.9 | 18.4 |  | 32 | -15
DAMAK-DUHABI | -10.5 | -7.5 | -5.9 | -4.9 | -5.7 | -13.3 | -18.7 | -27.6 | -41.1 | -45.2 | -46.2 | -43.8 | -38.5 | -29.4 | -19.5 | -22.4 | -18.7 | -21 | -20 | -20 | -32 | -37.1 | -47 | -50.3 | -43.7 | -41 | -27.2 | -25.5 | -21.2 | -13.6 | -10 |  | -4.9 | -50.3
HETAUDA-KAMANE | 23.3 | 24 | 23.8 | 23.1 | 25.4 | 26.7 | 27.6 | 27.6 | 29.7 | 11.8 | 11.7 | 11.9 | 12.2 | 11.4 | 14.5 | 25.4 | 30.1 | -32 | 32 | 32 | 10.7 | 11 | 12 | 12.4 | 12 | 11 | 10.2 | 9.9 | 10 | 17.3 | 26.1 |  | 32 | -32
MIRCHAIYA LAHAN 2 | 100.5 | 91.5 | 93.2 | 91.8 | 91.1 | 94.2 | 101.4 | 107.5 | 121.2 | 108.1 | 89.3 | 88.1 | 89.2 | 93.74 | 97.4 | 99.5 | 95.1 | 104 | 103 | 103 | 90 | 98.3 | 110 | 112.4 | 105.2 | 120 | 111.6 | 108.2 | 107.5 | 103.2 | 95.8 |  | 121.2 | 88.1
Water Level
UTK |  |  | 1984.22 | 1984.48 | 1984.7 | 1984.92 |  | 1985.12 |  | 1984.92 |  | 1984.42 | 1983.82 | 1983.7 | 1983.8 | 1983.79 | 1983.79 | 1983.79 | 1983.88 | 1984 | 1984.15 | 1984.25 | 1984.25 | 1984.2 | 1984.1 | 1983.98 | 1983.95 |  | 1983.77 | 1983.85 | 1984.08
KGA |  |  | 521.36 | 521.72 | 522.02 | 522.34 |  | 522.32 |  | 522.09 |  | 521.74 | 521.47 | 521.38 | 521.18 | 520.9 | 520.64 | 520.34 | 520.07 | 519.83 | 519.78 | 519.78 | 519.72 |  | 519.64 | 519.58 | 519.56 |  | 519.56 | 519.83 | 520.34
MMRS | 622.06 | 622.65 | 623.21 | 623.21 | 623.89 | 624.3 |  | 624.4 |  | 624.14 |  | 623.67 | 623.31 | 623.12 | 623.14 | 623.05 | 622.98 | 622.81 | 622.8 | 622.7 | 622.74 | 622.8 | 622.72 |  | 622.13 | 621.88 | 621.8 |  | 621.89 | 622.1 | 622.78
MRS | 334.72 | 335.28 | 335.67 | 336.06 | 336.35 | 336.61 |  | 336.65 |  | 336.39 |  | 336.01 | 335.63 | 335.01 | 334.58 | 334.17 | 334.17 | 334.42 | 334.97 | 335.16 | 335.34 | 335.45 | 335.54 |  | 335.28 | 335.17 | 335.14 |  | 335.19 | 335.23 | 335.39
CHM |  |  | 885.2 |  | 886.2 | 886.5 |  | 886.4 |  | 886.1 |  | 885.5 | 884.4 | 883.8 | 884.6 | 885.2 | 885.6 | 885.5 | 885.2 | 885.1 | 885.4 | 885.7 | 885.7 |  | 884.9 |  | 882.7 |  | 882.2 | 882.1 | 882.5
KL 1 | 0: 1518.95; 0.20833: 1518.96; 0.33333: 1518.96; 0.41667: 1518.96; 0.54167: 1518.97
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1795.79; 0.041667: 7:30
2
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/2); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/2)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1190.79; 0.66667: 1194.69; 0.70833: 1151.29; 0.72917: 1149.89; 0.75: 1168.69; 0.77083: 1266.59; 0.79167: 1340.39; 0.8125: 1433.79; 0.83333: 1588.89; 0.85417: 1719.89; 0.875: 1795.79; 0.91667: 1717.59; 0.95833: 1704.09 | 1650.79 | 1577.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1504.59 | 1307.49 | 1513.99 | 1672.89 | 1847.19 | 1803.85 | 1728.09 | 1683.59 | 1649.79 | 1353.99 | 1355.69 | 1268.99
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 3
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/3 |  |  | 2080/10/3 |  |  | Thursday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 566.6 | 566.8 | 553.78 | 591.6 | 564 | 647.6 | 657 | 734 | 499.8 | 371.2 | 315.3 | 498.7 | 498.7 | 498.7 | 733.5 | 700.6 | 813.8 | 703.9 | 756 | 596.3 | 580.7 | 461.6 | 372.7 | 268.9 | 255.6 | 433.1 | 470 | 525.8 | 587 | 579 | 675.4
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1852MW at 9:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1155 | 1281.49 | 1172.69 | 1166.79 | 1155.17 | 1192.99 | 1181.29 | 1281.79 | 1368.09 | 1487.99 | 1651.59 | 1677.59 | 1668.19 | 1851.59 | 1534.39 | 1254.39 | 1467.19 | 1434.29 | 1564.89 | 1482.69 | 1543.29 | 1309.29 | 1484.49 | 1718.09 | 1821.75 | 1773.85 | 1688.29 | 1640.69 | 1616.59 | 1414.19 | 1368.39 | 1249.39
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 29.5 | 29.5 | 29.5 | 29.9 | 29.9 | 29.8 | 29.8 | 29.1 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.8 | 28.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 86 | 29.9 | 28.4
Likhu-II(55) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 54 | 9.8 | 9.8
Super Dordi (54) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 54 | 10.3 | 10.3
Likhu-IV(52.4) | 16.5 | 16.5 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 14.4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52.4 | 17 | 14.4
Upper Marsyangdi "A"(50) | 29.1 | 29.1 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 50 | 29.1 | 28.2
Upper Bhotekoshi Khola(45) | 17.3 | 17.3 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 45 | 17.3 | 16.2
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14
Mistri Khola(42) | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 42 | 7.8 | 7
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.7 | 8.7 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 28 | 8.7 | 8.2
Dordi(27) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 30 | 6.4 | 6.4
Upper Madi(25) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 25 | 6.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 25 | 7.2 | 7.2
Solu Khola(23.5) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 23.5 | 7.6 | 7.6
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 22 | 10.4 | 10.4
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 22 | 22 | 24 | 24.5 | 23.9 | 23.9 | 23.7 | 21.8 | 21.5 | 20.4 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 240 | 24.5 | 18.9
Total IPP | 486.55 | 486.55 | 484.05 | 484.45 | 484.45 | 484.35 | 484.35 | 483.65 | 482.95 | 482.95 | 482.95 | 482.95 | 482.95 | 482.95 | 482.95 | 482.95 | 482.95 | 482.05 | 484.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 1042.4 | 486.55 | 482.05
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 190 | 250 | 250 | 0 | 0 | 0 | 0 | 30 | 76 | 76 | 40 | 30 | 230 | 300 | 320 | 350 | 180 | 180 | 100 | 60 | 20 | 456 | 350 | 0
Khimti Khola(60) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 30 | 30
Chilime(22.1) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.6 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22.1 | 15 | 10.2
Total NEA SUBSIDIARIES | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 100.2 | 230.2 | 290.2 | 290.2 | 40.2 | 40.2 | 40.2 | 40.2 | 70.6 | 116.2 | 116.2 | 80.2 | 70.2 | 270.2 | 340.2 | 365 | 395 | 225 | 225 | 145 | 105 | 65 | 538.1 | 395 | 40.2
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6 | 61 | 101.8 | 102.1 | 90 | 90 | 63.4 | 63.4 | 63.4 | 63.4 | 48.8 | 41.1 | 48 | 30.3 | 30.7 | 72.4 | 144.7 | 144.7 | 112.1 | 102 | 92 | 70 | 30 | 0 | 144 | 144.7 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 60 | 50 | 46 | 46 | 47 | 47 | 25 | 25 | 25.6 | 25.6 | 35 | 22 | 22 | 35 | 69 | 69 | 60 | 35 | 35 | 35 | 25 | 0 | 70 | 69 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 16 | 22.9 | 44.9 | 32.8 | 69.1 | 60 | 62.6 | 62.6 | 21 | 21 | 21 | 21 | 22.3 | 22 | 22.4 | 15.4 | 16.9 | 67.7 | 68.8 | 68.8 | 62.2 | 62.2 | 62.2 | 62 | 50 | 35 | 69 | 69.1 | 0
U Trisuli 3A(60) | 39.6 | 39.6 | 37 | 37 | 37 | 37 | 37 | 37 | 37.3 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 40.1 | 39 | 37 | 39.6 | 39.6 | 36.8 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 60 | 40.1 | 36
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 10 | 0 | 0 | 0 | 0 | 0 | 15 | 28 | 22 | 22 | 22 | 15 | 10 | 10 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 12 | 11.5 | 4.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 14.1 | 9.3 | 8.4
MODI(14) | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 14 | 3.4 | 3.3
SUN(10.05) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 10.05 | 2.5 | 2.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 4.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.54
Total ROR | 79.34 | 79.34 | 76.74 | 76.74 | 76.74 | 92.74 | 109.64 | 187.24 | 230.84 | 318.64 | 313.24 | 299.74 | 299.74 | 232.54 | 232.54 | 210.54 | 210.54 | 198.44 | 177.94 | 185.44 | 147.14 | 147.94 | 250.64 | 373.2 | 387.2 | 332.04 | 296.94 | 286.94 | 257.74 | 190.74 | 120.74 | 489.91 | 387.2 | 76.74
KL1(60) | 0.79167: 12.2; 0.8125: 0 | 60 | 12.2 | 0
KL2(32) | 0.79167: 3.6; 0.8125: 0 | 32 | 3.6 | 0
KL3(14) | 0.79167: 1.3; 0.8125: 0 | 14 | 1.3 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 17.1 | 0
TANAKPUR | 64.3 | 63.1 | 69.3 | 61 | 67.6 | 69 | 65.6 | 70 | 61 | 52.8 | 43.5 | 90.2 | 57.1 | 57.1 | 57.1 | 64.5 | 52.7 | 43.8 | 53.9 | 67 | 65.7 | 56.6 | 68 | 69.5 | 41.9 | 36 | 55.1 | 58 | 62.8 | 64 | 58 |  | 90.2 | 36
KATAIYA | 0: 0; 0.041667: 0; 0.083333: 0; 0.8125: 0 |  | 0 | 0
MUJAFFARPUR | 381 | 420.5 | 422.5 | 417.78 | 446 | 385 | 430 | 449 | 456 | 305 | 215 | 109 | 335 | 335 | 335 | 433 | 416 | 524 | 409 | 450 | 360 | 398 | 291 | 225 | 150 | 161 | 317 | 350 | 390 | 386 | 383 |  | 524 | 109
RAMNAGAR | 45.6 | 58 | 58 | 58 | 60 | 60 | 60 | 53 | 46 | 25 | 17 | 29.1 | 23.4 | 23.4 | 23.4 | 65 | 61.2 | 62.5 | 59 | 57 | 57 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 52 | 56 |  | 65 | 7
RAXAUL 132 | 120 | 25 | 17 | 17 | 18 | 50 | 92 | 85 | 93 | 55 | 32 | 32 | 28 | 28 | 28 | 100 | 106 | 114.5 | 114 | 112 | 62 | 56 | 30 | 0 | 0 | 0 |  |  |  | 20 | 22 |  | 120 | 0
NANPARA(33kV) | 0.8125: 0 |  | 0 | 0
BISHANPUR(33kV) | 0.8125: 0 |  | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | 0.8125: 0 |  | 0 | 0
RAJBIRAJ(33kV) | 0.8125: 0 |  | 0 | 0 |  | Line1
RAXAUL(33kV) | 0.8125: 0 |  | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 64.5 | 0 | 0 | [5 empty] | 78 | 62 | 63.7 | 55 | 55.2 | 55.2 | 55.2 | 71 | 64.7 | 69 | 68 | 70 | 51.6 | 63.1 | 65.6 | 71.2 | 70 | 51.6 | 54 | 55 | 66 | 65 | 60 |  | 78 | 0
Total IMPORT | 675.4 | 566.6 | 566.8 | 553.78 | 591.6 | 564 | 647.6 | 657 | 734 | 499.8 | 371.2 | 315.3 | 498.7 | 498.7 | 498.7 | 733.5 | 700.6 | 813.8 | 703.9 | 756 | 596.3 | 580.7 | 461.6 | 372.7 | 268.9 | 255.6 | 433.1 | 470 | 525.8 | 587 | 579 | 0 | 813.8 | 255.6
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1281.49 | 1172.69 | 1167.79 | 1155.17 | 1192.99 | 1181.29 | 1281.79 | 1368.09 | 1487.99 | 1401.59 | 1397.59 | 1388.19 | 1571.59 | 1254.39 | 1254.39 | 1467.19 | 1434.29 | 1564.89 | 1482.69 | 1543.29 | 1309.29 | 1284.49 | 1468.09 | 1571.75 | 1523.85 | 1468.29 | 1440.69 | 1467.59 | 1414.19 | 1368.39 | 1250.39 | 2231.81 | 1571.75 | 1155.17
Interruption/Tripping | 0.29167: 250; 0.3125: 280; 0.33333: 280; 0.375: 280; 0.41667: 280; 0.72917: 200; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 220; 0.83333: 200; 0.85417: 150; 0.875: 0 |  | 280 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1281.49 | 1172.69 | 1167.79 | 1155.17 | 1192.99 | 1181.29 | 1281.79 | 1368.09 | 1487.99 | 1651.59 | 1677.59 | 1668.19 | 1851.59 | 1534.39 | 1254.39 | 1467.19 | 1434.29 | 1564.89 | 1482.69 | 1543.29 | 1309.29 | 1484.49 | 1718.09 | 1821.75 | 1773.85 | 1688.29 | 1640.69 | 1617.59 | 1414.19 | 1368.39 | 1250.39 | 1693.71 | 1851.59 | 1155.17
TOTAL NATIONAL LOAD (ACTUAL) | 1281.49 | 1172.69 | 1166.79 | 1155.17 | 1192.99 | 1181.29 | 1281.79 | 1368.09 | 1487.99 | 1651.59 | 1677.59 | 1668.19 | 1851.59 | 1534.39 | 1254.39 | 1467.19 | 1434.29 | 1564.89 | 1482.69 | 1543.29 | 1309.29 | 1484.49 | 1718.09 | 1821.75 | 1773.85 | 1688.29 | 1640.69 | 1616.59 | 1414.19 | 1368.39 | 1249.39 |  | 1851.59 | 1155.17
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 |  | 1 | 0
Total EXPORT | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 |  | 1 | 0
NET IMPORT | 675.4 | 566.6 | 565.8 | 553.78 | 591.6 | 564 | 647.6 | 657 | 734 | 499.8 | 371.2 | 315.3 | 498.7 | 498.7 | 498.7 | 733.5 | 700.6 | 813.8 | 703.9 | 756 | 596.3 | 580.7 | 461.6 | 372.7 | 268.9 | 255.6 | 433.1 | 469 | 525.8 | 587 | 578 |  | 813.8 | 255.6
HZ | 49.97 | 49.98 | 50.02 | 49.973 | 50.04 | 49.952 | 49.989 | 50.014 | 50.064 | 50.057 | 50.037 | 50.06 | 50.038 | 50.038 | 49.99 | 50.003 | 50.051 | 50.027 | 49.943 | 50.065 | 49.953 | 50.111 | 50.01 | 49.999 | 50.082 | 50.024 | 50.057 | 50.04 | 49.99 | 50.01 | 49.95 |  | 50.111 | 49.943
HTD 132KV | 129.7 | 128.1 | 129.7 | 129.8 | 128.6 | 129.4 | 127.2 | 126.9 | 126.3 | 127.7 | 125.9 | 126.1 | 127.1 | 127.1 | 123.9 | 122.8 | 125.5 | 124.7 | 122.7 | 122.1 | 128.2 | 126.5 | 126 | 125.7 | 127.7 | 126.9 | 126.1 | 127 | 127 | 127 | 127 |  | 129.8 | 122.1
SUI 132KV | 132.8 | 131.8 | 133.4 | 133.1 | 132.4 | 132.7 | 130.7 | 130.1 | 128.8 | 128.9 | 126.9 | 127.1 | 129.3 | 129.3 | 125.7 | 125.6 | 128 | 127.4 | 125.9 | 125.4 | 130 | 128.4 | 127.4 | 127 | 128.8 | 130.4 | 128.7 | 129 | 129 | 129 | 129 |  | 133.4 | 125.4
DUBI 132KV | 130.3 | 130 | 131.4 | 128.8 | 127.5 | 130.5 | 127.5 | 129 | 125.5 | 129.2 | 132.6 | 131.1 | 132.5 | 132.5 | 127.4 | 126.8 | 126.8 | 126.5 | 127.7 | 127.8 | 131.4 | 128.2 | 126.2 | 129.1 | 130.9 | 130.6 | 126.4 | 128 | 128 | 128 | 128 |  | 132.6 | 125.5
ANAMANI 132KV | 132.5 | 131.9 | 133.5 | 129.5 | 128.6 | 129.9 | 127.5 | 128.3 | 126.9 | 128.8 | 132.6 | 130.4 | 132.4 | 132.4 | 128 | 128.7 | 129.3 | 127.9 | 129.1 | 128.6 | 131.5 | 129.3 | 125.8 | 129.1 | 131.7 | 132.1 | 129.6 | 131 | 131 | 131 | 131 |  | 133.5 | 125.8
KG-A 132KV | 131.5 | 132.3 | 128.9 | 134.8 | 132.5 | 131.3 | 130.6 | 131.7 | 133.1 | 132.7 | 131.4 | 132.3 | 131.4 | 131.4 | 130 | 130.5 | 134.2 | 132 | 130.7 | 132.3 | 135.3 | 132.6 | 133.8 | 131.3 | 134.2 | 135.5 | 136.9 | 137 | 137 | 137 | 137 |  | 137 | 128.9
KOHALPUR 132KV | 131.5 | 128.5 | 128.5 | 128.1 | 134.1 | 134.7 | 129.9 | 133.6 | 133.5 | 132.6 | 128 | 132.3 | 132.8 | 132.8 | 128.4 | 128.4 | 128.2 | 131.5 | 131.5 | 133.9 | 126.8 | 129.6 | 127.5 | 127.3 | 127.8 | 128.6 | 131.2 | 131 | 131 | 131 | 131 |  | 134.7 | 126.8
SUI 66KV | 66.9 | 66.6 | 66.6 | 67.1 | 66.7 | 66.6 | 65.7 | 65.2 | 64.4 | 64.6 | 63.7 | 63.7 | 65 | 65 | 63..5 | 63 | 64.8 | 63.6 | 63.4 | 62.8 | 65.5 | 64.5 | 64.4 | 63.9 | 64.3 | 65.3 | 64.3 | 64.3 | 64.3 | 64.3 | 64.3 |  | 67.1 | 62.8
[33 empty] | 0 | 0
Kathmandu Load | 158.98 | 142.28 | 172.62 | 137.64 | 146.96 | 168.62 | 199.32 | 247 | 302.58 | 352.328 | 397.34 | 392.94 | 365.14 | 365.14 | 42 | 294.84 | 280.84 | 301.508 | 311.286 | 322.56 | 325.775 | 331.504 | 415.108 | 455.032 | 433.643 | 417.757 | 383.44 | 373.64 | 373.64 | 242.64 | 180.64 |  | 455.032 | 42
MRS-SYU | -9.2 | -11.8 | -9.5 | -7.5 | -10.3 | -8 | -6 | 7.9 | 26.3 | 44.1 | 37.9 | 42.9 | 30.2 | 30.2 | 23.1 | 21.5 | 22.8 | 18.2 | 14.4 | 12.2 | 18.9 | 13.6 | 34.7 | 48.1 | 49.8 | 39.8 | 39.4 | 38 | 38 | 26 | 11 | 75 | 49.8 | -11.8
NMRS-MATA | -14.2 | -15.8 | -13.8 | -10.6 | -15 | -14.3 | -12 | 6.9 | 32.8 | 60.4 | 48.8 | 56.1 | 44 | 44 | 28 | 26.4 | 29.1 | 22.2 | 16.8 | 12.1 | 26.8 | 19 | 45.6 | 65.8 | 68.3 | 54.4 | 53 | 51 | 51 | 37 | 17 | 240 | 68.3 | -15.8
KL2-MATA | -10.4 | -33.1 | 2.4 | -35 | -32 | -6.5 | -1.2 | 5.9 | 18 | 29.2 | 48 | 40 | 37 | 37 | 23 | 20 | 12 | 14.3 | 17.9 | 25 | 37 | 40 | 56 | 50 | 42 | 48.4 | 33 | 33 | 33 | -10 | -25 | 240 | 56 | -35
KL1-SYU | -8.6 | -12 | -13.1 | -12.6 | -12.2 | -9.2 | -4.5 | 0 | 3.8 | 17.5 | 25.1 | 24 | 19 | 19 | 7 | 7 | 7 | 5.9 | 4.4 | 4.3 | 17.3 | 19.7 | 23.7 | 35.7 | 29.3 | 28.7 | 24 | 24 | 24 | 2 | 0 | 60 | 35.7 | -13.1
KHIMTI-LAMOSANGHU | 110.24 | 123.84 | 118.08 | 114.8 | 127.92 | 118.08 | 134.48 | 137.76 | 132.84 | 111.588 | 147.6 | 140 | 145 | 145 | 135 | 130 | 120 | 137.268 | 156.646 | 177.02 | 134.435 | 148.964 | 167.668 | 166.332 | 155.143 | 158.817 | 146.4 | 140 | 140 | 100 | 90 | 120 | 177.02 | 90
LAMOSHANGU-BHAKTAPUR | 81.6 | 89.5 | 86.5 | 82.1 | 88.9 | 83.8 | 91.1 | 92.98 | 91 | 79 | 97.2 | 92 | 93 | 93 | 95 | 96 | 89 | 90.6 | 100.4 | 111 | 90 | 96.2 | 104.2 | 104.1 | 99.2 | 101.2 | 98 | 97 | 97 | 84 | 72
BALAJU-SYUCHATAR | 53.5 | 80 | 75.9 | 71.4 | 77 | 54.5 | 57.9 | 42.6 | 10.9 | -40 | -29.2 | -34 | -24 | -24 | 15 | 22 | 28 | 20.5 | 39.1 | 40 | -3.5 | 2.3 | -36.1 | -37 | -41.1 | -29.5 | -23.4 | -20 | -20 | 20 | 40
DHALKE-NAWALPUR I | 75.2 | 114.5 | 105.2 | 96.2 | 105.2 | 76.6 | 89 | 87.4 | 84 | 63.6 | 79.8 | 66.8 | 68.7 | 68.7 | 96 | 87 | 85 | 82.1 | 100.1 | 106 | 82 | 88.6 | 84.8 | 82.3 | 74 | 107 | 89 | 90 | 90 | 89 | 90 |  | 114.5 | 63.6
N. BHARATPUR-BARDGHAT I | 26.7 | 26.1 | 24.7 | 22.5 | 25.9 | 29.5 | 29.6 | 20.7 | 0 | -8.3 | -3.8 | -9 | -4 | -4 | 3.1 | 6.5 | 4.6 | 9.2 | 9.9 | 6.4 | 1.7 | 6.7 | -3.8 | -12.1 | -10.8 | 2.2 | -5.3 | -3 | -3 | 0 | 0 |  | 29.6 | -12.1
DAMAK-DUHABI | 7.8 | -6.7 | -4.7 | -3.1 | -4.7 | -7.6 | -12.9 | -19.6 | -28.8 | -35.5 | -40.5 | -40.8 | -28.2 | -28.2 | -23.5 | -19 | -16 | -23.2 | -16.9 | -27.4 | -32.4 | -34.6 | -53.3 | -49.8 | -41.8 | -38.2 | -28.1 | -25 | -25 | -12 | -7 |  | 7.8 | -53.3
HETAUDA-KAMANE | 26.2 | 25.5 | 25.2 | 26.2 | 23.6 | 23.6 | 25.5 | 24.9 | 26.2 | 10 | 10.3 | 11.3 | 10.9 | 10.9 | 24.2 | 25.5 | 27.5 | 28.2 | 30.2 | 30.6 | 11.6 | 10.3 | 12.6 | 13.1 | 12.2 | 12.1 | 10.6 | 10 | 10 | 16 | 27 |  | 30.6 | 10
MIRCHAIYA LAHAN 2 | 96.3 | 91.1 | 86.5 | 84.5 | 92.3 | 86.6 | 98.4 | 95.3 | 109.1 | 97.6 | 78.7 | 75 | 62.5 | 62.5 | 113 | 100 | 105 | 101.3 | 96.7 | 110 | 91.8 | 94.5 | 115.1 | 118.3 | 105 | 104.2 | 108.3 | 115 | 115 | 105 | 99 |  | 118.3 | 62.5
Water Level
UTK | 1984.32 | 1984.52 | 1984.77 | 1985 | 1985.2 | 1985.45 |  | 1985.62 |  | 1985.85 |  | 1985.45 | 1985.22 | 1985.42 | 1985.63 | 1985.83 | 1985.94 | 1986.05 | 1986.12 | 1986.12 | 1986.12 |  | 1986.1 |  | 1985.57 |  | 1984.8 | 1984.52 | 1984.51 | 1984.55 | 1984.63
KGA | 520.61 | 520.98 | 521.32 | 521.66 | 521.98 | 522.3 |  | 522.55 |  | 522.5 |  | 522.23 | 522 | 521.94 | 521.87 | 521.79 | 521.74 | 521.76 | 521.82 | 521.92 | 521.98 |  | 522.1 |  | 521.74 |  | 521.28 |  | 521.02 |  | 521.27
MMRS | 623.28 | 623.51 | 623.93 | 624.19 | 624.66 | 624.9 |  | 625.05 |  | 624.83 |  | 624.44 | 324.32 | 624.06 | 623.79 | 623.51 | 623.46 | 623.41 | 623.41 | 623.48 | 623.44 |  | 623.5 |  | 622.86 |  | 622.56 |  | 622.51 | 622.38
MRS | 335.68 | 336.21 | 336.58 | 336.84 | 337.06 | 337.16 |  | 337.08 |  | 336.9 |  | 336.42 | 335.94 | 335.64 | 335.52 | 335.41 | 335.41 | 335.67 | 335.97 | 336.21 | 336.44 |  | 336.64 |  | 336.48 |  | 336.22 |  | 335.94 |  | 335.53
CHM | 883.5 | 884 | 884.6 | 885.2 | 885.8 | 886.3 |  | 886.3 |  | 886.2 |  | 885.6 |  |  | 885.4 | 885.4 |  | 884.3 | 885.3 | 886.1 | 886.4 |  | 886.9 |  | 886.4 |  | 885.2 |  |  |  | 884.4
KL 1 | 0.58333: 1518.99; 0.79167: 1518.99
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1851.59; 0.041667: 9:00
3
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/3); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/3)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1281.49; 0.66667: 1172.69; 0.70833: 1167.79; 0.72917: 1155.17; 0.75: 1192.99; 0.77083: 1181.29; 0.79167: 1281.79; 0.8125: 1368.09; 0.83333: 1487.99; 0.85417: 1651.59; 0.875: 1677.59; 0.91667: 1668.19; 0.95833: 1851.59 | 1534.39 | 1254.39 | 1467.19 | 1434.29 | 1564.89 | 1482.69 | 1543.29 | 1309.29 | 1484.49 | 1718.09 | 1821.75 | 1773.85 | 1688.29 | 1640.69 | 1617.59 | 1414.19 | 1368.39 | 1250.39
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 4
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/4 |  |  | 2080/10/4 |  |  | Friday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 568 | 549 | 538.6 | 531.9 | 560.2 | 593.5 | 560.5 | 609 | 387.7 | 459.3 | 411.9 | 394.6 | 591.9 | 610 | 633.7 | 645 | 670.6 | 681.9 | 718.1 | 586.6 | 586.6 | 360.5 | 377.4 | 312.9 | 338.7 | 368.583 | 517.5 | 565.5 | 611.1 | 621.3 | 534
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1729MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1145 | 1185.39 | 1219.39 | 1200.39 | 1144.99 | 1173.29 | 1201.59 | 1353.59 | 1396.59 | 1449.39 | 1555.69 | 1728.69 | 1491.44 | 1258.49 | 1435.54 | 1453.14 | 1467.84 | 1458.14 | 1482.54 | 1525.54 | 1543.54 | 1585.54 | 1560.54 | 1585.34 | 1731.14 | 1699.04 | 1676.44 | 1602.273 | 1517.29 | 1461.19 | 1379.69 | 1299.99
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 29.8 | 28.8 | 28.8 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | 29.2 | 29.2 | 29.2 | 29.2 | 30.6 | 86 | 30.6 | 28.1
Likhu-II(55) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.85 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 9.9 | 9.8
Super Dordi (54) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 54 | 10.3 | 10.3
Likhu-IV(52.4) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 52.4 | 17 | 14.9
Upper Marsyangdi "A"(50) | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28.2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 50 | 28.3 | 28
Upper Bhotekoshi Khola(45) | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 45 | 17.1 | 15.8
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14
Mistri Khola(42) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 42 | 7.9 | 7.8
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 28 | 8.2 | 8.2
Dordi(27) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 30 | 6.4 | 6.4
Upper Madi(25) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 25 | 6.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 25 | 7.2 | 7.2
Solu Khola(23.5) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 23.5 | 7.6 | 7.6
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 22 | 10.4 | 10.4
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 22 | 22 | 22 | 22 | 22 | 22 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 240 | 22 | 18.8
Total IPP | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 485.65 | 482.25 | 482.25 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 481.6 | 484.15 | 484.15 | 484.15 | 484.15 | 485.55 | 1042.4 | 485.65 | 481.6
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 60 | 260 | 260 | 260 | 100 | 130 | 80 | 20 | 90 | 90 | 90 | 70 | 30 | 30 | 175 | 255 | 245 | 210 | 140 | 70 | 30 | 80 | 50 | 456 | 260 | 0
Khimti Khola(60) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26.5 | 26.5 | 26.5 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27.6 | 27.6 | 27.6 | 27.6 | 27.6 | 60 | 30 | 26.5
Chilime(22.1) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 22.1 | 15 | 10.2
Total NEA SUBSIDIARIES | 45 | 45 | 45 | 45 | 45 | 45 | 95 | 125 | 105 | 305 | 305 | 296.7 | 136.7 | 166.7 | 117.2 | 57.2 | 127.2 | 127.2 | 127.2 | 107.2 | 67.2 | 67.2 | 212.2 | 292.2 | 282.2 | 247.2 | 177.9 | 107.8 | 67.8 | 117.8 | 87.8 | 538.1 | 305 | 45
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 61 | 71 | 91.6 | 91.6 | 101.25 | 80 | 60 | 96 | 126 | 60 | 61.5 | 71.4 | 71.5 | 61.1 | 61.1 | 112 | 111.8 | 142.2 | 141.1 | 140.6 | 64.7 | 57.2 | 30 | 0 | 144 | 142.2 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 50 | 45 | 45 | 45 | 45 | 30 | 25 | 35 | 50 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 60 | 60 | 60 | 47 | 30 | 23 | 23 | 0 | 70 | 60 | 0
MRS(69) | 45 | 45 | 45 | 0 | 0 | 0 | 23.7 | 23.7 | 35 | 35 | 35 | 43.4 | 24 | 18 | 17.7 | 17.7 | 17.7 | 17.8 | 39.5 | 46.2 | 35.2 | 35.2 | 58.8 | 67.9 | 67.9 | 66.5 | 66.5 | 35.8 | 35 | 35.1 | 22.8 | 69 | 67.9 | 0
U Trisuli 3A(60) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38.5 | 38.5 | 38.5 | 38.5 | 38.5 | 38.5 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 35 | 35 | 35 | 37.1 | 37.3 | 37.1 | 37.3 | 37.3 | 41.3 | 60 | 41.3 | 35
CHM(30) | 0 | 0 | 0 | 0 | 10 | 10 | 15 | 15 | 23 | 30 | 30 | 29 | 29 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 10 | 15 | 27 | 15 | 10 | 0 | 0 | 0 | 0 | 30 | 30 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 4.7 | 4.7 | 13.6 | 16.9 | 16.9 | 16.9 | 14.8 | 10.9 | 5.9 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16.9 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 0
DEVI(14.1) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10.8 | 10.8 | 10.8 | 14.1 | 10.8 | 8.4
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.4 | 3.4 | 3.4 | 14 | 3.4 | 3.3
SUN(10.05) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 10.05 | 2.5 | 2.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 120.74 | 120.74 | 120.74 | 75.74 | 110.74 | 110.74 | 179.44 | 225.44 | 249.74 | 277.34 | 278.74 | 300.59 | 244.94 | 195.34 | 244.34 | 295.34 | 204.34 | 203.14 | 234.84 | 236.64 | 200.14 | 175.14 | 281.04 | 329.94 | 372.34 | 359.94 | 341.64 | 207.84 | 193.74 | 166.64 | 105.34 | 489.91 | 372.34 | 75.74
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 62 | 65 | 67 | 69.6 | 63.8 | 64.2 | 72.5 | 72.6 | 66 | 62.3 | 69.2 | 62.5 | 62 | 59.6 | 68.1 | 74 | 62.8 | 59.6 | 61 | 64.8 | 68.1 | 68.1 | 60.4 | 63.7 | 56.9 | 53 | 50.083 | 69.7 | 47.7 | 61 | 60.7 |  | 74 | 47.7
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 390 | 420 | 400 | 388 | 391.7 | 420 | 402 | 372.1 | 400 | 202 | 263 | 234 | 200 | 395 | 388 | 415 | 426 | 423.3 | 424.2 | 462.1 | 402 | 402 | 201 | 202.1 | 154 | 173.6 | 197.7 | 322 | 368.4 | 368 | 391.1 |  | 462.1 | 154
RAMNAGAR | 60 | 60 | 60 | 57 | 54 | 52 | 48 | 48 | 42 | 25 | 25 | 28 | 29.6 | 30.2 | 42 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 0
RAXAUL 132 | 22 | 23 | 22 | 24 | 22.4 | 24 | 22 | 22.2 | 24 | 25 | 25 | 13 | 32 | 32.6 | 32.6 | 32 | 90 | 114.8 | 120.8 | 121.2 | 56.4 | 56.4 | 29.6 | 31.6 | 31 | 43.4 | 54.8 | 60 | 80 | 110 | 102 |  | 121.2 | 13
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 45.6 | 77 | 73.4 | 77.1 | 74.4 | 71 | 74.5 | 79.3 | 64.7 | 66.2 | 72.9 | 75.9 | 70 | 60.1 | 60.1 | 69.5 | 80 | 71 | 68.7 | 66 | 65.8 | 69.4 | 72.1 | 67.5 |  | 80 | 0
Total IMPORT | 534 | 568 | 549 | 538.6 | 531.9 | 560.2 | 593.5 | 560.5 | 609 | 387.7 | 459.3 | 411.9 | 394.6 | 591.9 | 610 | 633.7 | 645 | 670.6 | 681.9 | 718.1 | 586.6 | 586.6 | 360.5 | 377.4 | 312.9 | 338.7 | 368.583 | 517.5 | 565.5 | 611.1 | 621.3 | 0 | 718.1 | 312.9
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1185.39 | 1219.39 | 1200.39 | 1144.99 | 1173.29 | 1201.59 | 1353.59 | 1396.59 | 1449.39 | 1455.69 | 1528.69 | 1491.44 | 1258.49 | 1435.54 | 1453.14 | 1467.84 | 1458.14 | 1482.54 | 1525.54 | 1543.54 | 1335.54 | 1310.54 | 1335.34 | 1481.14 | 1449.04 | 1427.44 | 1372.273 | 1317.29 | 1311.19 | 1379.69 | 1299.99 | 2231.81 | 1543.54 | 1144.99
Interruption/Tripping | 0.29167: 100; 0.3125: 200; 0.70833: 250; 0.72917: 250; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 230; 0.85417: 200; 0.875: 150 |  | 250 | 100
TOTAL SYSTEM LOAD (EXPECTED) | 1185.39 | 1219.39 | 1200.39 | 1144.99 | 1173.29 | 1201.59 | 1353.59 | 1396.59 | 1449.39 | 1555.69 | 1728.69 | 1491.44 | 1258.49 | 1435.54 | 1453.14 | 1467.84 | 1458.14 | 1482.54 | 1525.54 | 1543.54 | 1585.54 | 1560.54 | 1585.34 | 1731.14 | 1699.04 | 1677.44 | 1602.273 | 1517.29 | 1461.19 | 1379.69 | 1299.99 | 1693.71 | 1731.14 | 1144.99
TOTAL NATIONAL LOAD (ACTUAL) | 1185.39 | 1219.39 | 1200.39 | 1144.99 | 1173.29 | 1201.59 | 1353.59 | 1396.59 | 1449.39 | 1555.69 | 1728.69 | 1491.44 | 1258.49 | 1435.54 | 1453.14 | 1467.84 | 1458.14 | 1482.54 | 1525.54 | 1543.54 | 1585.54 | 1560.54 | 1585.34 | 1731.14 | 1699.04 | 1676.44 | 1602.273 | 1517.29 | 1461.19 | 1379.69 | 1299.99 |  | 1731.14 | 1144.99
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
NET IMPORT | 534 | 568 | 549 | 538.6 | 531.9 | 560.2 | 593.5 | 560.5 | 609 | 387.7 | 459.3 | 411.9 | 394.6 | 591.9 | 610 | 633.7 | 645 | 670.6 | 681.9 | 718.1 | 586.6 | 586.6 | 360.5 | 377.4 | 312.9 | 337.7 | 368.583 | 517.5 | 565.5 | 611.1 | 621.3 |  | 718.1 | 312.9
HZ | 50.05 | 49.95 | 49.98 | 49.993 | 49.948 | 49.927 | 50.013 | 50.032 | 50.033 | 50.063 | 50.021 | 50.126 | 49.948 | 50.032 | 50.032 | 50.052 | 50.06 | 50.03 | 50.04 | 50.16 | 49.94 | 49.96 | 50.02 | 50.01 | 49.97 | 50.05 | 50.097 | 49.976 | 50.0002 | 50.018 | 49.873 |  | 50.16 | 49.873
HTD 132KV | 127 | 127 | 126 | 127.9 | 128.5 | 127 | 124.6 | 125.8 | 123.9 | 128.7 | 123.6 | 123.3 | 123.8 | 124 | 124 | 124.1 | 123 | 122.6 | 123.8 | 122.6 | 127.5 | 127.1 | 129.2 | 126.8 | 127.2 | 128.5 | 129.3 | 129.4 | 128.8 | 127.8 | 127.5 |  | 129.4 | 122.6
SUI 132KV | 132 | 132 | 131.5 | 132.6 | 133.2 | 131.3 | 129 | 129.4 | 127.3 | 129.7 | 125 | 124.5 | 125.4 | 125.8 | 125.8 | 126.3 | 126 | 125.8 | 126.8 | 125.6 | 129.6 | 128.8 | 129.9 | 127.8 | 127.8 | 129.4 | 130.3 | 130.8 | 130.7 | 130.5 | 130.9 |  | 133.2 | 124.5
DUBI 132KV | 127 | 127 | 128 | 128.5 | 130.1 | 126.3 | 131.5 | 126.3 | 126 | 129.8 | 129.2 | 126.3 | 128.6 | 127.6 | 127.6 | 126 | 126.6 | 127.2 | 126.3 | 123.8 | 129.3 | 130.3 | 130.4 | 128.1 | 131.1 | 130.4 | 130.7 | 132.2 | 128.8 | 128.5 | 128.3 |  | 132.2 | 123.8
ANAMANI 132KV | 128 | 128 | 130 | 129.4 | 130.6 | 128.1 | 134.3 | 129 | 127.7 | 131.1 | 130 | 126 | 129.2 | 128.2 | 128.2 | 128.6 | 128.7 | 129.6 | 128.5 | 125.4 | 130.6 | 131.7 | 130.1 | 127.5 | 131.8 | 131.6 | 133 | 134.5 | 130.3 | 130.7 | 130.8 |  | 134.5 | 125.4
KG-A 132KV | 134 | 134 | 131 | 131.4 | 132.8 | 133.3 | 129.8 | 131.6 | 130.1 | 134.2 | 131.6 | 131.3 | 132.5 | 132.6 | 132.6 | 132.5 | 130.7 | 134 | 133.1 | 131.3 | 135.1 | 135.2 | 135.5 | 134 | 133.5 | 134.9 | 135.7 | 137 | 136.7 | 132.8 | 131.9 |  | 137 | 129.8
KOHALPUR 132KV | 138 | 138 | 132 | 132.2 | 130 | 130.1 | 131.9 | 133.4 | 129.7 | 133.7 | 127.7 | 129.4 | 128.1 | 132.6 | 132.6 | 129.5 | 135.1 | 124.8 | 134 | 133.2 | 133.4 | 132.9 | 133.6 | 133.8 | 133.5 | 133.1 | 132.6 | 133.6 | 134.2 | 130.7 | 132.9 |  | 138 | 124.8
SUI 66KV | 66 | 66 | 66 | 66.5 | 67 | 65.9 | 64.7 | 65.1 | 64.1 | 65.2 | 62.6 | 62.5 | 62.9 | 63 | 63 | 63.5 | 63 | 63.5 | 63.5 | 63 | 64.9 | 64.8 | 65.4 | 64 | 64.1 | 65 | 65.4 | 65.7 | 65.3 | 65.5 | 65.8 |  | 67 | 62.5
[33 empty] | 0 | 0
Kathmandu Load | 129.64 | 111.24 | 110.24 | 117.26 | 129.54 | 170.14 | 207.84 | 237.04 | 274.84 | 355.98 | 392.84 | 397.02 | 363.44 | 350.988 | 42 | 308.34 | 268.04 | 302.98 | 294.14 | 305.86 | 312.68 | 328.12 | 365.9 | 422.6 | 423.16 | 409 | 388.204 | 359.975 |  | 267.222 | 202.633 |  | 423.16 | 42
MRS-SYU | 6 | -4 | -3 | -11.8 | -5.8 | 3.4 | 14.7 | 23.4 | 29.4 | 32.6 | 30.3 | 34.6 | 23.6 | 22.4 | 45.4 | 36.5 | 12.7 | 11.2 | 16.7 | 15.7 | 13.9 | 15.5 | 41.5 | 48.2 | 52.7 | 55.9 | 58.6 | 29.8 | 26.5 | 11 | -2.6 | 75 | 58.6 | -11.8
NMRS-MATA | 11 | -3.4 | -1.4 | -12 | -2.4 | 5.1 | 21.4 | 32 | 37.8 | 46.3 | 41.7 | 47.7 | 33.8 | 32.3 | 91.3 | 49 | 14.4 | 12.1 | 19.8 | 16.8 | 18.3 | 20.3 | 55.7 | 64.2 | 70.6 | 75.5 | 78.7 | 40 | 31.5 | 11.4 | -7.2 | 240 | 91.3 | -12
KL2-MATA | -45 | -44 | -46 | -35 | -40 | -33 | -29 | -21 | -6 | 28 | 44 | 39.3 | 33 | 27.1 | 4.6 | -1.5 | 12 | 14.2 | 9.3 | 13.8 | 33.9 | 37.9 | 41 | 50.2 | 50.6 | 44 | 39.5 | 44 | 35 | 6.5 | -8.8 | 240 | 50.6 | -46
KL1-SYU | -10 | -10 | -12 | -9.5 | -9.1 | -8.2 | -10.1 | -5 | -2 | 20 | 23 | 22.5 | 19.2 | 20.3 | 10.3 | 6.8 | 1.4 | 1.7 | -0.5 | 7.4 | 18.4 | 20 | 24.4 | 27.9 | 28.2 | 26.6 | 23.4 | 22.5 | 15.7 | 6.7 | -3.2 | 60 | 28.2 | -12
KHIMTI-LAMOSANGHU | 80 | 85 | 85 | 97.92 | 99.2 | 115.2 | 123.2 | 120 | 128 | 141.44 | 164.8 | 159.08 | 160 | 144.648 | 119.884 | 110 | 120 | 159.04 | 148 | 156.32 | 137.44 | 143.68 | 116.16 | 144.96 | 133.92 | 117.76 | 98.564 | 134.435 | 137.274 | 141.282 | 130.093 | 120 | 164.8 | 80
LAMOSHANGU-BHAKTAPUR | 75 | 81 | 77 | 75 | 76 | 82 | 86 | 85 | 90 | 95 | 107 | 101.2 | 96.8 | 95.6 | 82.3 | 89 | 103 | 103.8 | 97.2 | 101.5 | 92.8 | 95.9 | 82.1 | 96 | 90.2 | 82 | 72.3 | 89 | 90.3 | 93.4 | 88.1
BALAJU-SYUCHATAR | 63 | 80 | 77 | 64.3 | 62 | 57.3 | 39 | 24.1 | 20 | -12.3 | -10 | -13.8 | 2.6 | 3.2 | -9.5 | 8 | 43 | 43.1 | 32.5 | 35.2 | 15.8 | 14.3 | -31.9 | -41.5 | -51.4 | -60.7 | -66.3 | -16.6 | 4.1 | 41.8 | 70.2
DHALKE-NAWALPUR I | 95 | 101 | 92 | 84 | 93 | 97 | 102 | 88 | 98 | 84 | 92 | 90.3 | 87 | 93.6 | 84.7 | 98 | 94 | 99.7 | 90.5 | 94.7 | 80.5 | 85.3 | 61.9 | 71.5 | 66 | 57.1 | 50.2 | 76.3 | 79.8 | 86 | 82.2 |  | 102 | 50.2
N. BHARATPUR-BARDGHAT I | 15 | 28 | 25 | 21 | 22 | 11 | 5 | 0 | -8 | -11.2 | -10 | -13.2 | -5 | -5 | -25.3 | -16 | 12 | 14.8 | 16.7 | 19.4 | 8 | 8 | 0 | 0 | 0 | -12.6 | -15.2 | 0 | 4.1 | 18.2 | 22.5 |  | 28 | -25.3
DAMAK-DUHABI | -6 | -7 | -4 | -3 | -4.5 | -8.1 | -19 | -21.2 | -27.3 | -37 | -41 | -41.2 | -28 | -27.2 | -20.9 | -17 | -18 | -19 | -22.1 | -23.4 | -30.6 | -30.6 | -45.1 | -49 | -42 | -37.5 | -31.5 | -24.8 | -19.7 | -14.1 | -8.5 |  | -3 | -49
HETAUDA-KAMANE | 26 | 26 | 26 | 27 | 26.1 | 28 | 27 | 29.1 | 27.3 | 12.8 | 13 | 13 | 13 | 13 | 20.1 | 24 | 32 | 32.4 | 31.9 | 29.6 | 11.4 | 11.4 | 10 | 11.1 | 10.6 | 11.2 | 10 | 10.2 | 12.3 | 19.1 | 26.6 |  | 32.4 | 10
MIRCHAIYA LAHAN 2 | 93 | 88 | 91 | 89 | 86 | 100 | 95 | 103 | 98.3 | 98 | 99 | 97.4 | 87 | 86.5 | 106.9 | 113 | 105 | 103.6 | 112.6 | 110.6 | 94.5 | 94.5 | 90.7 | 98.7 | 93 | 99.3 | 96.7 | 90.2 | 93.1 | 103.1 | 99.6 |  | 113 | 86
Water Level
UTK | 1984.9 | 1985.1 | 1985.3 | 1985.55 | 1985.75 | 1985.95 | 1986 | 1986.02 | 1986.02 | 1985.83 | 1985.55 | 1985.3 | 1984.82 | 1984.52 | 1984.54 | 1984.54 | 1984.5 | 1984.45 | 1984.38 | 1984.32 | 1984.39 |  | 1984.4 |  | 1983.92 | 1983.6 | 1983.49 |  | 1983.5 | 1983.62 | 1983.72
KGA | 521.61 | 521.96 | 522.224 | 522.56 | 522.86 | 523.12 | 523.25 | 523.25 | 523.28 | 523.16 | 523.04 | 522.9 | 522.7 | 522.6 | 522.55 | 522.14 | 521.7 | 521.48 | 521.45 | 521.35 | 521.22 |  | 521.12 |  | 520.68. |  | 519.88 |  | 519.62 | 519.64 | 519.9
MMRS | 622.96 | 623.39 | 623.84 | 624.24 | 624.46 | 624.46 | 624.45 | 624.35 | 624.21 | 624.11 | 623.99 | 623.87 | 623.6 | 623.63 | 623.65 | 623.28 | 622.99 | 622.83 | 622.85 | 622.91 | 623.01 |  | 623.35 | 623.17 | 622.97 |  | 622.39 |  | 622.16 | 622.31 | 622.31
MRS | 335.44 | 335.57 | 335.58 | 335.69 | 336 | 336.28 | 336.35 | 336.36 | 336.32 | 336.27 | 336.17 | 336.07 | 335.77 | 335.52 | 335.45 | 335.51 | 335.82 | 336.11 | 336.32 | 336.29 | 336.24 |  | 336.49 |  | 336.31 |  | 335.97 |  | 335.76 | 335.72 | 335.74
CHM | 885 | 885.5 | 886 | 886.5 | 886.9 | 886.8 | 886.8 | 886.6 | 886.2 | 885.7 | 884.9 | 884.4 | 883.5 | 883.9 | 884.7 | 884.7 | 884 | 883.9 | 883.9 | 883.7 | 884 |  | 884.3 |  | 883.7 |  | 882.1 |  | 882.8 | 883.7 | 884.3
KL 1 | 0: 1519; 0.83333: 1519.03
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1728.69; 0.041667: 7:30
4
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/4); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/4)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1185.39; 0.66667: 1219.39; 0.70833: 1200.39; 0.72917: 1144.99; 0.75: 1173.29; 0.77083: 1201.59; 0.79167: 1353.59; 0.8125: 1396.59; 0.83333: 1449.39; 0.85417: 1555.69; 0.875: 1728.69; 0.91667: 1491.44; 0.95833: 1258.49 | 1435.54 | 1453.14 | 1467.84 | 1458.14 | 1482.54 | 1525.54 | 1543.54 | 1585.54 | 1560.54 | 1585.34 | 1731.14 | 1699.04 | 1677.44 | 1602.273 | 1517.29 | 1461.19 | 1379.69 | 1299.99
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 5
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/5 |  |  | 2080/10/5 |  |  | Saturday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 595 | 577.2 | 588.4 | 626 | 643.8 | 573 | 575.8 | 597.1 | 353.4 | 351.6 | 280.7 | 332.2 | 477.7 | 516.9 | 603.4 | 616.1 | 593 | 642 | 649.1 | 501.3 | 523.2 | 276.4 | 396.5 | 180.4 | 195.7 | 339.7 | 316 | 547 | 519.6 | 536 | 592.8
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1643MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1182 | 1222.59 | 1224.79 | 1181.59 | 1192.79 | 1230.19 | 1274.19 | 1258.79 | 1309.09 | 1415.59 | 1576.69 | 1643.29 | 1641.19 | 1555.29 | 1490.69 | 1523.09 | 1385.59 | 1368.29 | 1326.59 | 1319.09 | 1330.19 | 1391.99 | 1483.59 | 1453.09 | 1818.69 | 1675.59 | 1630.69 | 1624.69 | 1600.99 | 1366.89 | 1232.09 | 1183.49
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 30.6 | 30.6 | 29.1 | 29.1 | 29.1 | 29.1 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 27.8 | 28.4 | 21.8 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 86 | 30.6 | 21.8
Likhu-II(55) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 9.9 | 9.9
Super Dordi (54) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 54 | 10.3 | 10.2
Likhu-IV(52.4) | 14.9 | 14.9 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 52.4 | 15.4 | 14.9
Upper Marsyangdi "A"(50) | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 50 | 28.7 | 28.3
Upper Bhotekoshi Khola(45) | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 17.1 | 1
Super Madi ( 44 ) | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 14
Mistri Khola(42) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 42 | 7.9 | 7.9
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 28 | 8.2 | 8.2
Dordi(27) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 30 | 6.4 | 6.4
Upper Madi(25) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 25 | 6.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 25 | 7.2 | 7.2
Solu Khola(23.5) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 23.5 | 7.6 | 7.6
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 22 | 10.4 | 10.4
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(20) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 14 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 26.2 | 23.3 | 23.3 | 21.8 | 21.8 | 22.3 | 23.2 | 19 | 19.9 | 19.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 240 | 26.2 | 19
Total IPP | 485.55 | 485.55 | 484.55 | 484.55 | 484.55 | 484.55 | 471.15 | 471.15 | 471.15 | 471.15 | 471.15 | 471.15 | 479.45 | 484.05 | 477.45 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 482.85 | 1042.4 | 485.55 | 471.15
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 65 | 300 | 260 | 290 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 70 | 300 | 360 | 280 | 130 | 130 | 15 | 15 | 0 | 456 | 360 | 0
Khimti Khola(60) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 60 | 28 | 28
Chilime(22.1) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10 | 10 | 10 | 22.1 | 10.3 | 10
Total NEA SUBSIDIARIES | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 53.3 | 53.3 | 103.3 | 338.3 | 298.3 | 328.3 | 228.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.2 | 38.2 | 38.2 | 38.2 | 68.2 | 108.2 | 338.2 | 398.2 | 318.2 | 168.2 | 168.2 | 53 | 53 | 38 | 538.1 | 398.2 | 38
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 61 | 61.2 | 61.2 | 81 | 98.1 | 91.4 | 62.2 | 61.8 | 48 | 48 | 48.9 | 30.6 | 30.6 | 20.8 | 30.8 | 141.9 | 144.5 | 144.5 | 144.5 | 144.5 | 144.5 | 93.4 | 30 | 30 | 144 | 144.5 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 35 | 50 | 50 | 60 | 43 | 43 | 43 | 45 | 45 | 35 | 0 | 0 | 0 | 25 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 68.9 | 50 | 25 | 0 | 70 | 68.9 | 0
MRS(69) | 22.9 | 22.9 | 0 | 0 | 0 | 16 | 16 | 32.5 | 45.8 | 45.8 | 33.6 | 45.3 | 33 | 33 | 33 | 32 | 32 | 33.2 | 33.2 | 32.7 | 17.7 | 23.3 | 45 | 47.9 | 47.9 | 67.7 | 67.7 | 67.7 | 51 | 32 | 17 | 69 | 67.7 | 0
U Trisuli 3A(60) | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 38.5 | 38.5 | 38.3 | 38.3 | 39 | 40 | 38 | 38 | 37.8 | 38 | 38 | 30 | 30 | 39.6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37.8 | 37.8 | 37.8 | 60 | 40 | 30
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 23 | 28 | 28 | 23 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 10 | 23 | 23 | 23 | 23 | 10 | 10 | 0 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 8.1 | 12.6 | 13 | 16.2 | 16.2 | 13.6 | 10.4 | 5.3 | 1.3 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16.2 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 8.2 | 8.5 | 8.6 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 14.1 | 9.8 | 8.2
MODI(14) | 5 | 5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.5 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 14 | 5 | 3.3
SUN(10.05) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10.05 | 4 | 4
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 106.04 | 106.04 | 81.64 | 81.64 | 81.44 | 107.64 | 161.34 | 208.84 | 244.04 | 263.84 | 272.24 | 311.04 | 265.34 | 240.64 | 240.44 | 231.04 | 231.04 | 212.54 | 156.04 | 160.04 | 119.64 | 159.34 | 335.64 | 351.14 | 364.14 | 383.94 | 383.94 | 383.94 | 284.04 | 176.64 | 126.64 | 489.91 | 383.94 | 81.44
KL1(60) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 | 60 | 0 | 0
KL2(32) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 | 32 | 0 | 0
KL3(14) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 67.4 | 64 | 66.4 | 71.4 | 74 | 63.2 | 66.4 | 65.8 | 63.5 | 63 | 64.6 | 61.1 | 61.5 | 61.5 | 64.7 | 65.8 | 58.8 | 60.2 | 64.3 | 53.4 | 47.3 | 56.1 | 56.5 | 66.3 | 58.5 | 57.3 | 67.3 | 67 | 56 | 55.6 | 45 |  | 74 | 45
KATAIYA | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0 |  | 0 | 0
MUJAFFARPUR | 365 | 370 | 359.8 | 412 | 442 | 460 | 402 | 412 | 391 | 195 | 251 | 186 | 238 | 378.5 | 403.8 | 390 | 403 | 375 | 387.8 | 421.8 | 345.6 | 359.8 | 112.6 | 209.8 | 47.1 | 65.9 | 205.3 | 205 | 435 | 392 | 413 |  | 460 | 47.1
RAMNAGAR | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0 |  | 0 | 0
RAXAUL 132 | 116 | 110 | 101 | 105 | 110 | 120.6 | 104.6 | 98 | 105.2 | 54.3 | 0 | 0 |  |  |  | 102 | 103.6 | 109.6 | 112.8 | 104.8 | 53.4 | 49 | 45.2 | 47.2 | 0 | 0 | 0 | 0 | 12 | 16 | 18 |  | 120.6 | 0
NANPARA(33kV) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 |  | 0 | 0
BISHANPUR(33kV) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 |  | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 |  | 0 | 0
RAJBIRAJ(33kV) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 |  | 0 | 0 |  | Line1
RAXAUL(33kV) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0 |  | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 44.4 | 51 | 50 | 0 |  | 0 |  |  | 37.4 | 41.1 | 36 | 33.6 | 32.7 | 37.7 | 48.4 | 45.6 | 50.7 | 48.2 | 77.1 | 69.1 | 55 | 58.3 | 62.1 | 73.2 | 74.8 | 72.5 | 67.1 | 44 | 44 | 56 | 60 |  | 77.1 | 0
Total IMPORT | 592.8 | 595 | 577.2 | 588.4 | 626 | 643.8 | 573 | 575.8 | 597.1 | 353.4 | 351.6 | 280.7 | 332.2 | 477.7 | 516.9 | 603.4 | 616.1 | 593 | 642 | 649.1 | 501.3 | 523.2 | 276.4 | 396.5 | 180.4 | 195.7 | 339.7 | 316 | 547 | 519.6 | 536 | 0 | 649.1 | 180.4
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1222.59 | 1224.79 | 1181.59 | 1192.79 | 1230.19 | 1274.19 | 1258.79 | 1309.09 | 1415.59 | 1426.69 | 1393.29 | 1391.19 | 1305.29 | 1240.69 | 1273.09 | 1355.59 | 1368.29 | 1326.59 | 1319.09 | 1330.19 | 1141.99 | 1233.59 | 1203.09 | 1568.69 | 1425.59 | 1380.69 | 1374.69 | 1350.99 | 1366.89 | 1232.09 | 1183.49 | 2231.81 | 1568.69 | 1141.99
Interruption/Tripping | 0.29167: 150; 0.3125: 250; 0.33333: 250; 0.375: 250; 0.41667: 250; 0.45833: 250; 0.5: 30; 0.70833: 250; 0.72917: 250; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 250 |  | 250 | 30
TOTAL SYSTEM LOAD (EXPECTED) | 1222.59 | 1224.79 | 1181.59 | 1192.79 | 1230.19 | 1274.19 | 1258.79 | 1309.09 | 1415.59 | 1576.69 | 1643.29 | 1641.19 | 1555.29 | 1490.69 | 1523.09 | 1385.59 | 1368.29 | 1326.59 | 1319.09 | 1330.19 | 1391.99 | 1483.59 | 1453.09 | 1818.69 | 1675.59 | 1630.69 | 1624.69 | 1600.99 | 1366.89 | 1232.09 | 1183.49 | 1693.71 | 1818.69 | 1181.59
TOTAL NATIONAL LOAD (ACTUAL) | 1222.59 | 1224.79 | 1181.59 | 1192.79 | 1230.19 | 1274.19 | 1258.79 | 1309.09 | 1415.59 | 1576.69 | 1643.29 | 1641.19 | 1555.29 | 1490.69 | 1523.09 | 1385.59 | 1368.29 | 1326.59 | 1319.09 | 1330.19 | 1391.99 | 1483.59 | 1453.09 | 1818.69 | 1675.59 | 1630.69 | 1624.69 | 1600.99 | 1366.89 | 1232.09 | 1183.49 |  | 1818.69 | 1181.59
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
NET IMPORT | 592.8 | 595 | 577.2 | 588.4 | 626 | 643.8 | 573 | 575.8 | 597.1 | 353.4 | 351.6 | 280.7 | 332.2 | 477.7 | 516.9 | 603.4 | 616.1 | 593 | 642 | 649.1 | 501.3 | 523.2 | 276.4 | 396.5 | 180.4 | 195.7 | 339.7 | 316 | 547 | 519.6 | 536 |  | 649.1 | 180.4
HZ | 50.019 | 50 | 50.007 | 49.9745 | 49.953 | 49.859 | 50.002 | 49.943 | 50.016 | 50.024 | 50.072 | 50.089 | 50.036 | 49.974 | 50.17 | 50.062 | 49.995 | 50.081 | 50 | 50 | 49.98 | 50.02 | 49.92 | 49.8 | 49.86 | 49.96 | 49.934 | 49.934 | 50.03 | 49.895 | 50.092 |  | 50.17 | 49.8
HTD 132KV | 129.5 | 129.4 | 130.4 | 127.6 | 125.1 | 127 | 128.3 | 126.8 | 124.5 | 129.3 | 126.3 | 125.4 | 124.8 | 125.5 | 126.4 | 125.5 | 126.2 | 126.3 | 126.6 | 125.3 | 130.1 | 129.2 | 130 | 127.8 | 127.8 | 128 | 127.7 | 127.7 | 127.4 | 128.4 | 128 |  | 130.4 | 124.5
SUI 132KV | 132.9 | 132.8 | 133.3 | 131.2 | 129 | 130.4 | 131.5 | 130.4 | 127.4 | 130.7 | 127.9 | 126.7 | 126.4 | 127.4 | 128.1 | 128.5 | 129 | 129.4 | 129.4 | 128.4 | 132.1 | 130.9 | 131.1 | 128.7 | 128.7 | 130 | 129.8 | 129.8 | 130.4 | 131.6 | 132 |  | 133.3 | 126.4
DUBI 132KV | 128.7 | 130 | 130.9 | 128 | 127.9 | 126.4 | 129.4 | 128.5 | 125.3 | 129.5 | 126.4 | 128.5 | 132.3 | 131 | 130 | 127 | 128.6 | 129.6 | 128.9 | 129.7 | 131.4 | 126.5 | 129.7 | 122.9 | 122.9 | 132.4 | 130.2 | 130.2 | 127.6 | 130.6 | 128.7 |  | 132.4 | 122.9
ANAMANI 132KV | 131.5 | 132 | 132.9 | 131.3 | 131.1 | 129.7 | 131.7 | 130.4 | 130.3 | 132.1 | 128.5 | 128.9 | [8 empty] | 130.8 | 125.3 | 127.9 | 122.5 | 122.5 | 132.4 | 131.6 | 131.6 | 131 | 134.1 | 132.6 |  | 134.1 | 122.5
KG-A 132KV | 133.8 | 133 | 133.5 | 131.3 | 128.3 | 129.8 | 132.3 | 133.8 | 130.5 | 135.6 | 134.2 | 133.3 | 131.9 | 132.1 | 131.7 | 131.7 | 133.4 | 133.5 | 133.2 | 134 | 136.3 | 135.5 | 135.3 | 132.9 | 132.9 | 133.5 | 133.7 | 133.7 | 136 | 133.2 | 31 |  | 136.3 | 31
KOHALPUR 132KV | 133.3 | 134.8 | 135.4 | 131.7 | 127.9 | 126.6 | 128.8 | 130.3 | 127.5 | 131.7 | 125.3 | 133 | 129.3 | 125.3 | 133.7 | 129.9 | 130.5 | 134.5 | 134.9 | 132.3 | 137.5 | 131.3 | 132.2 | 130.6 | 130.6 | 133.4 | 132.3 | 132.3 | 132 | 130.2 | 131.7 |  | 137.5 | 125.3
SUI 66KV | 67.2 | 67 | 67.3 | 66.4 | 65.2 | 65.8 | 66.3 | 65.8 | 64.2 | 66 | 64.5 | 63.8 | 63.6 | 64.1 | 64.4 | 64.7 | 65.2 | 65.3 | 65.4 | 64.7 | 66.6 | 65.8 | 65.6 | 64.3 | 64.3 | 65 | 65 | 65 | 65.3 | 66.2 | 66.3 |  | 67.3 | 63.6
[33 empty] | 0 | 0
Kathmandu Load | 171.182 | 153.522 | 150.544 | 150.648 | 167.912 | 173.52 | 194.672 | 235.372 | 271.136 | 299.48 | 343.168 | 360.764 | 373.424 | 350.92 | 42 | 293.78 | 279.988 | 266.158 | 256.7 | 254.54 | 270.42 | 283.28 | 335.08 | 378.38 | 396.78 | 377.06 | 409.04 | 414.04 | 293.14 | 181.84 | 166.94 |  | 414.04 | 42
MRS-SYU | 1.1 | -7 | -4.8 | -17.7 | -18 | -16.7 | -5.7 | 3.8 | 9.6 | 16.3 | 21 | 28.7 | 26.3 | 25.1 | 23.7 | 17.1 | 15.7 | 16.3 | 9.2 | 6.9 | 10.5 | 8.5 | 54.6 | 49.4 | 51.8 | 60.3 | 60.3 | 60.3 | 27.6 | 4.6 | 5 | 75 | 60.3 | -18
NMRS-MATA | -4.2 | -14.9 | -11.9 | -29.9 | -29.3 | -27.8 | -13 | 1.1 | 7.1 | 27.3 | 32.1 | 39.7 | 37.3 | 36.9 | 27.6 | 18.7 | 16.3 | 17.9 | 5.5 | 1.5 | 11.6 | 12.8 | 77.5 | 69.5 | 73.3 | 84.1 | 84.3 | 84.3 | 32.4 | 1.9 | 2.2 | 240 | 84.3 | -29.9
KL2-MATA | -16.2 | -17 | -19.3 | -14.9 | -11.2 | -9.3 | -9 | 0 | 5.5 | 20.6 | 28.4 | 27.7 | 33.6 | 30.9 | 27 | 13.6 | 12 | 9.4 | 13.6 | 11 | 27.6 | 30 | 25 | 38.5 | 29 | 20 | 18.6 | 18.6 | 15 | -20 | -26 | 240 | 38.5 | -26
KL1-SYU | -7.4 | -8.8 | -9 | -6.8 | -10.1 | -8.7 | -3 | -3.1 | 0.6 | 16 | 18.3 | 18.1 | 19.8 | 19.4 | 5.5 | 3.8 | -1.5 | -2.7 | 3.1 | -2.5 | 14.6 | 17 | 22.6 | 25.6 | 25.7 | 24.8 | 24.3 | 24.3 | 6.8 | -6 | -5.6 | 60 | 25.7 | -10.1
KHIMTI-LAMOSANGHU | 104.542 | 107.882 | 102.204 | 126.608 | 143.172 | 142.68 | 133.332 | 141.532 | 158.096 | 128.74 | 152.028 | 150.224 | 156.784 | 134.48 | 137.596 | 132.84 | 129.748 | 128.118 | 131.36 | 139.2 | 113.28 | 123.04 | 63.84 | 103.84 | 125.44 | 96.32 | 130 | 135 | 120 | 110 | 100 | 120 | 158.096 | 63.84
LAMOSHANGU-BHAKTAPUR | 76.1 | 77.4 | 75.5 | 87.7 | 98.7 | 95.2 | 90.5 | 93.4 | 101.6 | 88.1 | 99 | 97.8 | 101.6 | 88.5 | 92.6 | 89.4 | 85.2 | 87.5 | 88.7 | 95 | 80.6 | 83.7 | 53.9 | 74.1 | 85.8 | 71.6 | 64.4 | 64.4 | 92 | 85 | 81
BALAJU-SYUCHATAR | 57.3 | 71 | 68.8 | 32.7 | 31.7 | 80 | 64.8 | 48.7 | 41 | -2.6 | -5.3 | -13.8 | -8.3 | -15.8 | 4 | 22.2 | 23.7 | 31.2 | 37.1 | 40.5 | 6.3 | 2.1 | -65.5 | -54 | -42.8 | -56 | -59.9 | -59.9 | 12 | 55 | 58
DHALKE-NAWALPUR I | 74 | 73.4 | 70.9 | 96 | 102 | 95.6 | 93 | 88.5 | 92.3 | 68.5 | 91.4 | 84.5 | 101.1 | 87.2 | 84 | 82.8 | 82.2 | 83.3 | 85.7 | 93 | 68.7 | 72.5 | 30.9 | 52.6 | 62.9 | 51.7 | 52.7 | 52.7 | 95 | 90 | 94 |  | 102 | 30.9
N. BHARATPUR-BARDGHAT I | 21.1 | 23.2 | 21.6 | 32.8 | 37 | 35.1 | 30.8 | 23.4 | 18 | 11.8 | 7.7 | 5.4 | 5.3 | 8.7 | 12.9 | 20 | 13.8 | 30.4 | 15.4 | 15.9 | 8.8 | 8.7 | -16.1 | -11 | -12.9 | -14.1 | -13.9 | -13.9 | 6.8 | 17 | 15 |  | 37 | -16.1
DAMAK-DUHABI | -5.8 | -4.8 | -5.3 | 5.2 | -5.5 | -5.8 | -12.1 | -18.2 | -28.7 | -31 | -35.3 | -33.2 | -2.1 | -2.2 | 4.8 | 8 | 6.2 | 6 | 7.4 | 6 | -20.3 | -45.4 | -55.9 | -55.1 | -49.9 | -42.8 | -34.8 | -34.8 | -21 | -10 | -9.8 |  | 8 | -55.9
HETAUDA-KAMANE | 26.4 | 26.6 | 26.4 | 26.3 | 26.7 | 26.6 | 27.4 | 28 | 29.2 | 9.8 | 9.7 | 9.7 | 9.8 | 7.6 | 13.7 | 27.5 | 27.4 | 27.1 | 27.1 | 27.5 | 8.6 | 8.4 | 9.7 | 10 | 9.8 | 9.2 | 8.5 | 8.5 | 8 | 25 | 25 |  | 29.2 | 7.6
MIRCHAIYA LAHAN 2 | 90.1 | 83.6 | 84.4 | 80.7 | 93.1 | 89.4 | 86.7 | 87.8 | 99.3 | 89.5 | 90.8 | 90.4 | 55.4 | 52.2 | 68.9 | 63.4 | 72.5 | 69.8 | 69.6 | 68.7 | 68 | 79.7 | 90.1 | 106.9 | 106.4 | 98.7 | 99.2 | 99.2 | 104 | 92 | 88.9 |  | 106.9 | 52.2
Water Level
UTK | 1983.9 | 1984.2 | 1984.45 | 1984.66 | 1984.89 | 1985.11 |  | 1985.3 |  | 1985.12 |  | 1984.65 | 1984 | 1983.7 | 1983.98 | 1984.2 | 1984.4 | 1984.6 | 1984.8 | 1985 | 1985.2 |  | 1985.35 | 1985.26 | 1984.91 | 1984.55 | 1984.3 |  | 1984.3 | 1984.4 | 1984.55
KGA | 520.28 | 520.66 | 521.02 | 521.36 | 521.68 | 521.98 |  | 522.13 |  | 522.08 |  | 521.96 | 521.76 | 521.6 | 521.58 | 521.55 | 521.6 | 521.74 | 521.88 | 522 | 522.1 |  | 522.18 |  | 521.66 |  | 521 |  | 520.54 | 520.3 | 520.34
MMRS | 623.08 | 623.42 | 623.84 | 624.14 | 624.54 | 624.85 |  | 624.84 |  | 624.91 |  | 624.61 | 624.36 | 624.03 | 623.78 | 623.55 | 623.42 | 623.44 | 623.6 | 623.96 | 624.28 |  | 624.34 |  | 623.89 |  | 623.3 |  | 622.89 | 622.97 | 623.16
MRS | 335.78 | 336.18 | 336.6 | 336.91 | 337.13 | 337.33 |  | 337.37 |  | 337.22 |  | 337.02 | 336.75 | 336.56 | 336.35 | 336.15 | 335.97 | 336.17 | 336.34 | 336.44 | 336.53 |  | 336.71 |  | 336.64 |  | 336.29 |  |  | 335.73 | 335.64
CHM | 884.9 | 885.5 | 886 | 886.5 | 886.9 | 887.1 |  | 887.1 |  | 886.5 |  | 885.6 | 884.8 |  | 884.6 | 884.5 | 884.3 | 884.2 | 884.1 | 884.5 | 885.1 |  | 885.7 |  | 885.6 | 885 | 884.7 |  | 884.4 | 884.3 | 884.9
KL 1 | 0: 1519.04
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1643.29; 0.041667: 7:30
5
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/5); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/5)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1222.59; 0.66667: 1224.79; 0.70833: 1181.59; 0.72917: 1192.79; 0.75: 1230.19; 0.77083: 1274.19; 0.79167: 1258.79; 0.8125: 1309.09; 0.83333: 1415.59; 0.85417: 1576.69; 0.875: 1643.29; 0.91667: 1641.19; 0.95833: 1555.29 | 1490.69 | 1523.09 | 1385.59 | 1368.29 | 1326.59 | 1319.09 | 1330.19 | 1391.99 | 1483.59 | 1453.09 | 1818.69 | 1675.59 | 1630.69 | 1624.69 | 1600.99 | 1366.89 | 1232.09 | 1183.49
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 6
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/6 |  |  | 2080/10/6 |  |  | Sunday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 559.2 | 481 | 512.6 | 538.1 | 571 | 553.977 | 553.8 | 608 | 539.5 | 409 | 398.5 | 405.8 | 458.9 | 561 | 633.2 | 620 | 627 | 727.5 | 596 | 472.4 | 498.6 | 484.1 | 463.1 | 427.5 | 404.6 | 298.48 | 394.1 | 421.6 | 434.7 | 614.1 | 551
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1712MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1097 | 1167.09 | 1175.29 | 1097.09 | 1128.69 | 1154.19 | 1197.09 | 1306.067 | 1395.19 | 1480.79 | 1440.089 | 1425.29 | 1712.39 | 1610.89 | 1497.09 | 1395.39 | 1487.69 | 1471.99 | 1478.79 | 1531.89 | 1526.69 | 1303.79 | 1343.69 | 1540.29 | 1804.99 | 1751.95 | 1721.09 | 1548.37 | 1442.59 | 1340.09 | 1146.19 | 1241.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 86 | 27.2 | 27
Likhu-II(55) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 9.9 | 9.9
Super Dordi (54) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 54 | 10.2 | 10.2
Likhu-IV(52.4) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 52.4 | 15.4 | 15.4
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 50 | 28.7 | 28.7
Upper Bhotekoshi Khola(45) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 45 | 16.6 | 16.6
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16
Mistri Khola(42) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 42 | 7.9 | 7
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 30 | 8.4 | 7.8
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 28 | 8.2 | 8.2
Dordi(27) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 30 | 6.4 | 6.4
Upper Madi(25) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 25 | 6.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 25 | 7.2 | 7.2
Solu Khola(23.5) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 23.5 | 7.6 | 7.6
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 22.2 | 4.5 | 4.5
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 22 | 10.4 | 10.4
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 0: 22.9; 0.041667: 22.9; 0.083333: 22.9; 0.125: 22.9; 0.16667: 22.9; 0.20833: 22.9; 0.22917: 22.9; 0.25: 22.9; 0.27083: 22.9; 0.29167: 22.9; 0.3125: 22.9; 0.33333: 22.9; 0.375: 22.9; 0.41667: 22.9; 0.45833: 22.9; 0.5: 22.9; 0.54167: 22.9 | 240 | 22.9 | 22.9
Total IPP | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 498.45 | 484.45 | 484.45 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 484.25 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 1042.4 | 498.45 | 483.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 76 | 105 | 125 | 135 | 185 | 110 | 50 | 35 | 60 | 65 | 65 | 40 | 156 | 110 | 150 | 200 | 230 | 210 | 220 | 220 | 70 | 40 | 20 | 0 | 456 | 230 | 0
Khimti Khola(60) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 60 | 28 | 28
Chilime(22.1) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 22.1 | 10.2 | 10
Total NEA SUBSIDIARIES | 38 | 38 | 38 | 38 | 38 | 38 | 68 | 114 | 143 | 163 | 173 | 223 | 148 | 88.2 | 73.2 | 98.2 | 103.2 | 103.2 | 78.2 | 194.2 | 148.2 | 188.2 | 238.2 | 268.2 | 248.2 | 258.2 | 258.2 | 108.2 | 78.2 | 58.2 | 38.2 | 538.1 | 268.2 | 38
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 32.5 | 48 | 60 | 60.999 | 113 | 106.3 | 91.6 | 81 | 61 | 61 | 61.2 | 62 | 61 | 81.3 | 62.2 | 37.4 | 46 | 104 | 122 | 106 | 91.3 | 60.6 | 60.6 | 60.6 | 30.8 | 144 | 122 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 45 | 46 | 55 | 60 | 50 | 45 | 50 | 50 | 50 | 50 | 35 | 35 | 25 | 25 | 35 | 70 | 60 | 60 | 22 | 22 | 22 | 0 | 0 | 70 | 70 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 48.8 | 34.2 | 35 | 69.2 | 52.8 | 53.4 | 53.4 | 52.8 | 52.8 | 52 | 52 | 52 | 52 | 35.4 | 35.4 | 68.4 | 68.4 | 54 | 54 | 45.8 | 33.1 | 33.1 | 33.1 | 0 | 69 | 69.2 | 0
U Trisuli 3A(60) | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 39.3 | 40.3 | 40.3 | 40.3 | 41.3 | 38 | 38.3 | 38.3 | 42.3 | 42.3 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 60 | 42.3 | 36
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 15 | 10 | 15 | 23 | 23 | 10 | 15 | 15 | 13 | 13 | 13 | 10 | 0 | 0 | 0 | 10 | 23 | 30 | 30 | 23 | 15 | 15 | 0 | 0 | 30 | 30 | 0 | [16 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 4.5 | 7.5 | 11.2 | 14 | 14.6 | 14 | 14 | 9.6 | 9.6 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14.6 | 0 | [15 empty] | Tanakpur | 69 | 47 | 64.6 | 60.2 | 65 | 62 | 65.2 | 45.6 | 65.3 | 61.2 | 67.5 | 67 | 61 | 68 | 67.1 | 60 | 61.8 | 67 | 66.3 | 63.4 | 69.9 | 62.3 | 56.5 | 60
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [15 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4 | [15 empty] | Muz | 414 | 374 | 345 | 369 | 405 | 389 | 365 | 292 | 285 | 340 | 382 | 400 | 385 | 385 | 468 | 350 | 300 | 310 | 242 | 103.98 | 186 | 194.5 | 386 | 424
DEVI(14.1) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 14.1 | 9.8 | 9.8 | [15 empty] | Ram | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MODI(14) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 3.5 | 0 | [15 empty] | Rax | 14 | 60 | 103 | 108.9 | 101 | 102.8 | 56 | 0 | 0 | 0 | 40 | 98 | 110 | 110 | 122 | 122 | 60 | 55 | 64 | 81.6 | 103.6 | 102.6 | 107.4 | 15
SUN(10.05) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10.05 | 4 | 4 | [15 empty] | Sam | 62 | 0 | 0 | 0 | 0 | 0 | 53.3 | 60.9 | 55.5 | 57.7 | 71.5 | 68.2 | 64 | 64 | 70.4 | 64 | 50.6 | 52.1 | 55.2 | 49.5 | 62.1 | 75.3 | 64.2 | 52
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.54 | [16 empty] | 69 | 47 | 64.6 | 60.2 | 65 | 62 | 65.2 | 45.6 | 65.3 | 61.2 | 67.5 | 67 | 61 | 68 | 67.1 | 60 | 61.8 | 67 | 66.3 | 63.4 | 69.9 | 62.3 | 56.5 | 60
Total ROR | 79.64 | 79.64 | 79.64 | 79.64 | 79.64 | 89.64 | 185.64 | 228.94 | 231.34 | 239.139 | 344.84 | 326.44 | 292.64 | 285.74 | 276.94 | 272.04 | 264.54 | 265.34 | 241.94 | 252.24 | 198.94 | 172.64 | 233.74 | 339.74 | 342.3 | 324.34 | 257.74 | 206.34 | 206.34 | 169.34 | 106.44 | 489.91 | 344.84 | 79.64 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [16 empty] | 414 | 374 | 345 | 369 | 405 | 389 | 365 | 292 | 285 | 340 | 382 | 400 | 385 | 385 | 468 | 350 | 300 | 310 | 242 | 103.98 | 186 | 194.5 | 386 | 424
KL2(32) | [31 empty] | 32 | 0 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0 | [16 empty] | 14 | 60 | 103 | 108.9 | 101 | 102.8 | 56 | 0 | 0 | 0 | 40 | 98 | 110 | 110 | 122 | 122 | 60 | 55 | 64 | 81.6 | 103.6 | 102.6 | 107.4 | 15
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | [16 empty] | 62 | 0 | 0 | 0 | 0 | 0 | 53.3 | 60.9 | 55.5 | 57.7 | 71.5 | 68.2 | 64 | 64 | 70.4 | 64 | 50.6 | 52.1 | 55.2 | 49.5 | 62.1 | 75.3 | 64.2 | 52
TANAKPUR | 60 | 69.2 | 47 | 64.6 | 60.2 | 65 | 49.977 | 62 | 59 | 65.2 | 60.1 | 45.6 | 65.3 | 61.2 | 67.5 | 67 | 61 | 68 | 67.1 | 60 | 61.8 | 64.6 | 67 | 68.1 | 66.3 | 63.2 | 63.4 | 62.8 | 69.9 | 62.3 | 56.5 |  | 69.9 | 45.6
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 424 | 414 | 374 | 345 | 369 | 405 | 400 | 389 | 400 | 365 | 290 | 292 | 285 | 340 | 382 | 400 | 385 | 385 | 468 | 350 | 300 | 328 | 310 | 280 | 242 | 220 | 103.98 | 189.5 | 186 | 194.5 | 386 |  | 468 | 103.98
RAMNAGAR | [32 empty] | 0 | 0 | [23 empty] | 69 | 0 | 414 | 0 | 14 | 62
RAXAUL 132 | 15 | 14 | 60 | 103 | 108.9 | 101 | 104 | 102.8 | 103 | 56 | 0 | 0 |  |  | 40 | 98 | 110 | 110 | 122 | 122 | 60 | 54 | 55 | 60 | 64 | 69 | 81.6 | 84.2 | 103.6 | 102.6 | 107.4 |  | 122 | 0 | [23 empty] | 47 | 0 | 374 | 0 | 60 | 0
NANPARA(33kV) | [32 empty] | 0 | 0 | [23 empty] | 64.6 | 0 | 345 | 0 | 103 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test | [20 empty] | 60.2 | 0 | 369 | 0 | 108.9 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [23 empty] | 65 | 0 | 405 | 0 | 101 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1 | [21 empty] | 62 | 0 | 389 | 0 | 102.8 | 0
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2 | [21 empty] | 65.2 | 0 | 365 | 0 | 56 | 53.3
SAMPATIYA 132 kV | 52 | 62 | 0 | 0 |  |  |  |  | 46 | 53.3 | 58.9 | 60.9 | 55.5 | 57.7 | 71.5 | 68.2 | 64 | 64 | 70.4 | 64 | 50.6 | 52 | 52.1 | 55 | 55.2 | 52.4 | 49.5 | 57.6 | 62.1 | 75.3 | 64.2 |  | 75.3 | 0 | [23 empty] | 45.6 | 0 | 292 | 0 | 0 | 60.9
Total IMPORT | 551 | 559.2 | 481 | 512.6 | 538.1 | 571 | 553.977 | 553.8 | 608 | 539.5 | 409 | 398.5 | 405.8 | 458.9 | 561 | 633.2 | 620 | 627 | 727.5 | 596 | 472.4 | 498.6 | 484.1 | 463.1 | 427.5 | 404.6 | 298.48 | 394.1 | 421.6 | 434.7 | 614.1 | 0 | 727.5 | 298.48 | [23 empty] | 65.3 | 0 | 285 | 0 | 0 | 55.5
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [23 empty] | 61.2 | 0 | 340 | 0 | 0 | 57.7
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [23 empty] | 67.5 | 0 | 382 | 0 | 40 | 71.5
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [23 empty] | 67 | 0 | 400 | 0 | 98 | 68.2
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0 | [23 empty] | 61 | 0 | 385 | 0 | 110 | 64
TOTAL SYSTEM LOAD (ACTUAL) | 1167.09 | 1175.29 | 1097.09 | 1128.69 | 1154.19 | 1197.09 | 1306.067 | 1395.19 | 1480.79 | 1440.089 | 1425.29 | 1432.39 | 1330.89 | 1317.09 | 1395.39 | 1487.69 | 1471.99 | 1479.79 | 1531.89 | 1526.69 | 1303.79 | 1343.69 | 1440.29 | 1554.99 | 1501.95 | 1471.09 | 1298.37 | 1192.59 | 1190.09 | 1146.19 | 1242.69 | 2231.81 | 1554.99 | 1097.09 | [23 empty] | 68 | 0 | 385 | 0 | 110 | 64
Interruption/Tripping | 0.33333: 280; 0.375: 280; 0.41667: 180; 0.75: 100; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 250; 0.875: 150; 0.91667: 0; 0.95833: 0 |  | 280 | 0 | [23 empty] | 67.1 | 0 | 468 | 0 | 122 | 70.4
TOTAL SYSTEM LOAD (EXPECTED) | 1167.09 | 1175.29 | 1097.09 | 1128.69 | 1154.19 | 1197.09 | 1306.067 | 1395.19 | 1480.79 | 1440.089 | 1425.29 | 1712.39 | 1610.89 | 1497.09 | 1395.39 | 1487.69 | 1471.99 | 1479.79 | 1531.89 | 1526.69 | 1303.79 | 1343.69 | 1540.29 | 1804.99 | 1751.95 | 1721.09 | 1548.37 | 1442.59 | 1340.09 | 1146.19 | 1242.69 | 1693.71 | 1804.99 | 1097.09 | [23 empty] | 60 | 0 | 350 | 0 | 122 | 64
TOTAL NATIONAL LOAD (ACTUAL) | 1167.09 | 1175.29 | 1097.09 | 1128.69 | 1154.19 | 1197.09 | 1306.067 | 1395.19 | 1480.79 | 1440.089 | 1425.29 | 1712.39 | 1610.89 | 1497.09 | 1395.39 | 1487.69 | 1471.99 | 1478.79 | 1531.89 | 1526.69 | 1303.79 | 1343.69 | 1540.29 | 1804.99 | 1751.95 | 1721.09 | 1548.37 | 1442.59 | 1340.09 | 1146.19 | 1241.69 |  | 1804.99 | 1097.09 | [23 empty] | 61.8 | 0 | 300 | 0 | 60 | 50.6
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 67 | 0 | 310 | 0 | 55 | 52.1
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 66.3 | 0 | 242 | 0 | 64 | 55.2
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 63.4 | 0 | 103.98 | 0 | 81.6 | 49.5
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 69.9 | 0 | 186 | 0 | 103.6 | 62.1
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [23 empty] | 62.3 | 0 | 194.5 | 0 | 102.6 | 75.3
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 0 | [23 empty] | 56.5 | 0 | 386 | 0 | 107.4 | 64.2
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 0 | [23 empty] | 60 | 0 | 424 | 0 | 15 | 52
NET IMPORT | 551 | 559.2 | 481 | 512.6 | 538.1 | 571 | 553.977 | 553.8 | 608 | 539.5 | 409 | 398.5 | 405.8 | 458.9 | 561 | 633.2 | 620 | 626 | 727.5 | 596 | 472.4 | 498.6 | 484.1 | 463.1 | 427.5 | 404.6 | 298.48 | 394.1 | 421.6 | 434.7 | 613.1 |  | 727.5 | 298.48
HZ | 49.993 | 50.035 | 49.907 | 49.966 | 49.921 | 50 | 49.974 | 49.87 | 50.0086 | 50.164 | 49.97 | 50.057 | 50.062 | 49.995 | 50.078 | 50.018 | 50.064 | 50.064 | 50.06 | 49.85 | 49.85 | 49.985 | 50.029 | 50.007 | 49.9 | 50.021 | 50.06 | 50.05 | 49.98 | 50.06 | 50.03 |  | 50.164 | 49.85
HTD 132KV | 127.9 | 127.5 | 128.4 | 130.2 | 130.6 | 126.6 | 127 | 125.8 | 125.1 | 127.5 | 126 | 124.9 | 125.4 | 125.8 | 127 | 124.7 | 126.2 | 126.2 | 124.4 | 124.4 | 128.7 | 127.1 | 127.3 | 126.6 | 127.8 | 128.5 | 128.5 | 130.1 | 130.9 | 128.7 | 129.7 |  | 130.9 | 124.4
SUI 132KV | 131.9 | 131.7 | 132.2 | 134 | 133.6 | 130.5 | 130.6 | 128.9 | 128.4 | 129.6 | 127.7 | 126.8 | 127.5 | 127.9 | 128.7 | 127.1 | 128.5 | 128.5 | 127.4 | 127.4 | 130.4 | 128.9 | 128.9 | 127.5 | 128.7 | 129.5 | 129.5 | 131.3 | 132.1 | 131.3 | 132.8 |  | 134 | 126.8
DUBI 132KV | 0: 128.2; 0.041667: 129.4; 0.083333: 128.9 |  | 129.4 | 128.2
ANAMANI 132KV | 0: 133; 0.041667: 132.4; 0.083333: 131.8 |  | 133 | 131.8
KG-A 132KV | 133.2 | 132.6 | 129.2 | 132.6 | 134 | 130.7 | 131.4 | 133.3 | 132 | 135.5 | 133.8 | 133.6 | 133.3 | 132.2 | 133.5 | 133.1 | 134.8 | 134.8 | 133.6 | 133.6 | 135.1 | 133.5 | 134.3 | 133.5 | 134.3 | 135.7 | 135.7 | 135.7 | 135.7 | 131.3 | 134.3 |  | 135.7 | 129.2
KOHALPUR 132KV | 132 | 126.8 | 134.9 | 136 | 130.1 | 128.2 | 130.1 | 132.8 | 131.6 | 130.9 | 128.3 | 130.5 | 133.8 | 133.3 | 127.2 | 131.5 | 134.4 | 134.4 | 130.2 | 130.2 | 129.1 | 127 | 132.3 | 126.6 | 131.1 | 132.6 | 132.6 | 129.8 | 129.8 | 127.5 | 128.2 |  | 136 | 126.6
SUI 66KV | 66.4 | 66.2 | 66.6 | 67.2 | 67.4 | 65.7 | 65.5 | 64.8 | 64.6 | 65.2 | 64.3 | 63.6 | 64 | 64.1 | 64.5 | 63.7 | 64.5 | 64.5 | 64 | 64 | 65.4 | 64.6 | 64.6 | 63.7 | 64.7 | 65 | 65 | 65.7 | 65.7 | 65.9 | 65.9 |  | 67.4 | 63.6
[33 empty] | 0 | 0
Kathmandu Load | 141.04 | 137.34 | 124.24 | 168.448 | 141.968 | 179.928 | 201.096 | 247.968 | 287.36 | 336.972 | 377.244 | 379.16 | 356.997 | 343.56 | 42 | 327.86 | 309.74 | 309.74 | 298.64 | 282.14 | 314.24 | 332.74 | 371.74 | 414.68 | 419.98 | 397.54 | 370.4 | 346.3 | 322.72 | 247.5 | 175.8 |  | 419.98 | 42
MRS-SYU | -3.3 | -6 | -20 | -16.3 | -14.6 | -13.7 | -6 | 4.4 | 11.9 | 16.1 | 37.7 | 35.7 | 36.5 | 36.2 | 34.5 | 24.3 | 25.1 | 25.1 | 21.4 | 20 | 19.5 | 13.5 | 26 | 38.2 | 39.5 | 34 | 30.6 | 23.5 | 27.5 | 13.5 | 0.3 | 75 | 39.5 | -20
NMRS-MATA | -8 | -11 | -29.5 | -25.5 | -24 | -24.3 | -12.5 | 1.4 | 11.6 | 22.5 | 51.6 | 49.7 | 50.6 | 50.3 | 42.9 | 28.1 | 29.6 | 29.6 | 23.3 | 21 | 27.2 | 19.2 | 37 | 52.5 | 53.7 | 46 | 41.5 | 32.7 | 33.7 | 13.5 | -3.3 | 240 | 53.7 | -29.5
KL2-MATA | -30 | -32 | -12 | 16.6 | -14.6 | -6.8 | -3.4 | 0 | 8.6 | 30.5 | 32.2 | 32 | 26 | 23.2 | 24.8 | 13.8 | 12.5 | 12.5 | 12 | 17 | 28 | 37 | 40 | 51 | 55 | 51 | 45.7 | 45 | 36.4 | 7.8 | -8 | 240 | 55 | -32
KL1-SYU | -9 | -10 | -5.6 | -7.9 | -3.1 | -4.7 | -1.7 | 0.4 | 0.7 | 16.1 | 22.3 | 21.4 | 18.2 | 19.3 | 18.8 | 6.9 | 7.8 | 7.8 | 0.4 | 5 | 20 | 21 | 24 | 26.9 | 28.1 | 26 | 24.2 | 23.9 | 18.8 | 5.1 | -6.4 | 60 | 28.1 | -10
KHIMTI-LAMOSANGHU | 100 | 105 | 100 | 110.208 | 106.928 | 138.088 | 131.856 | 147.928 | 160.72 | 157.932 | 137.104 | 144.32 | 126.357 | 111.52 | 113.16 | 144.32 | 131.2 | 131.2 | 142.4 | 120 | 128 | 152 | 155.2 | 154.08 | 151.68 | 150.4 | 136.96 | 129.76 | 114.88 | 116.16 | 101.76 | 120 | 160.72 | 100
LAMOSHANGU-BHAKTAPUR | 82 | 82 | 82 | 78.7 | 77.3 | 96.1 | 90 | 97.1 | 101.5 | 101.4 | 92 | 94.5 | 85.7 | 78.5 | 80.4 | 95.9 | 89.2 | 89.2 | 95 | 103 | 89.5 | 101 | 103 | 101 | 101 | 100 | 92.7 | 88.6 | 81.5 | 82.7 | 75.9 |  | 103 | 75.9
BALAJU-SYUCHATAR | 70 | 73 | 80 | 74 | 70.4 | 76.6 | 59.2 | 95.8 | 37.8 | 9.3 | -23.2 | -17.4 | -18.8 | -18.7 | -10 | 19.2 | 16.7 | 16.7 | 27 | 31 | 6 | 14 | -5 | -29 | -32 | -24 | -18.8 | -13.1 | -9.7 | 25.6 | 46.3 |  | 95.8 | -32
DHALKE-NAWALPUR I | 97 | 95 | 79.5 | 77 | 71.5 | 96.3 | 97.6 | 95.3 | 97.5 | 92.9 | 82 | 87.9 | 78.9 | 71 | 69.3 | 89.4 | 81.5 | 81.5 | 91 | 98 | 77 | 87 | 89 | 81 | 78 | 78 | 68.4 | 71 | 95 | 73.98 | 69.1 |  | 98 | 68.4
N. BHARATPUR-BARDGHAT I | 14.6 | 17.5 | 32.7 | 28.7 | 28.9 | 31.7 | 26.5 | 24.6 | 16 | 13.3 | 0 | -1 | -3.1 | -1.2 | 5 | 10.8 | 8.7 | 8.7 | 11 | 9.4 | 9 | 11 | 11 | 4 | 0 | 2 | 0 | 4.9 | 5.6 | 10.8 | 14.8 |  | 32.7 | -3.1
DAMAK-DUHABI | 0: -7.2; 0.041667: -3; 0.083333: -4.2 |  | -3 | -7.2
HETAUDA-KAMANE | 25.4 | 25 | 25.6 | 25.2 | 25.6 | 24.8 | 25 | 26.6 | 27 | 11.7 | 12.3 | 12.2 | 12.1 | 12 | 12.3 | 22.9 | 25.9 | 25.9 | 20.3 | 21.6 | 12 | 12 | 12 | 13 | 12.1 | 12 | 10.4 | 9.8 | 9.8 | 20.5 | 20 |  | 27 | 9.8
MIRCHAIYA LAHAN 2 | 90.4 | 84 | 80.8 | 81.5 | 75.3 | 80.9 | 89.1 | 99.7 | 103.2 | 92.7 | 97.6 | 84.7 | 79 | 87.7 | 111.9 | 114.9 | 99.8 | 99.8 | 112 | 109 | 93 | 101 | 117 | 114 | 94 | 103 | 96 | 94.7 | 106.7 | 101.8 | 102.4 |  | 117 | 75.3
Water Level
UTK | 1984.8 | 1985.02 | 1985.25 | 1985.48 | 1985.68 | 1985.9 | 1986 | 1986 |  | 1985.9 |  | 1985.7 | 1985.43 | 1985.38 | 1985.41 | 1985.48 |  | 1985.44 | 1985.49 | 1985.35 |  | 1985.15 | 1985 |  | 1984.62 | 1984.45 | 1984.25 |  | 1984.22 | 1984.3 | 1984.5
KGA | 520.66 | 521.04 | 521.4 | 521.72 | 522.05 | 522.37 |  | 522.56 |  | 522.56 |  | 522.35 | 522.06 | 521.84 | 521.78 | 521.75 | 521.7 | 521.7 | 521.7 | 521.66 |  | 521.62 |  |  | 521.44 | 521.44 | 521.09 |  | 521 | 521.02 | 521.12
MMRS | 623.42 | 623.81 | 624.16 | 624.48 | 624.85 | 625.14 |  | 625.21 |  | 625.03 |  | 624.72 | 624.42 | 624.2 | 623.78 | 623.61 | 623.28 | 622.99 | 622.64 | 622.54 | 622.4 | 622.46 | 622.38 | 622.1 | 621.69 | 621.06 | 621.01 |  | 621.24 | 621.66 | 622.41
MRS | 335.62 | 336.24 | 336.72 | 337.08 | 337.32 | 337.55 |  | 337.51 |  | 337.38 |  | 337.04 | 336.64 | 336.3 | 335.96 | 335.58 | 335.33 | 335.34 | 335.34 | 335.36 | 335.41 | 335.48 | 335.55 | 335.48 | 335.42 | 335.39 | 335.38 |  | 335.42 | 335.47 | 335.56
CHM | 885.5 | 885.8 | 886.3 | 886.8 | 887.2 | 887.3 |  | 887.4 |  | 887.2 |  | 886.4 | 885.9 | 885.7 | 885.6 | 885.4 | 885.1 | 884.7 | 884.5 | 884.7 | 885.2 | 885.6 | 885.8 |  | 884.9 | 883.8 | 883.1 |  | 882.2 | 882.4 | 883.3
KL 1
Others IPP Detail
Upper Mai Khola(9.98) | 0.041667: 0.22; 0.083333: 0.23; 0.125: 0.23; 0.16667: 0.2; 0.20833: 0.22; 0.22917: 0.1; 0.25: 0 | 9.94
Kabeli B-1 Cascade(9.94) | 0.041667: 0.38; 0.083333: 0.36; 0.125: 0.32; 0.16667: 0.33; 0.20833: 0.32; 0.25: 0.19
Iwa Khola(9.9) | 0.041667: 0.39; 0.083333: 0.35; 0.125: 0.32; 0.16667: 0.37; 0.20833: 0.29; 0.25: 0.07
Sipring Khola(9.658) | 0.041667: 0.62; 0.083333: 0.48; 0.125: 0.36; 0.16667: 0.24; 0.20833: 0.23
Super Mai 'A' (9.6) | 0.125: 88.8889; 0.22917: 1.56
Mai Beni(9.51) | 0.20833: 2.05; 0.22917: 2.32
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 1.61 | 1.42 | 90.1189 | 1.14 | 3.11 | 3.98 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1712.39; 0.041667: 8:00
6
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/6); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/6)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1167.09; 0.66667: 1175.29; 0.70833: 1097.09; 0.72917: 1128.69; 0.75: 1154.19; 0.77083: 1197.09; 0.79167: 1306.067; 0.8125: 1395.19; 0.83333: 1480.79; 0.85417: 1440.089; 0.875: 1425.29; 0.91667: 1712.39; 0.95833: 1610.89 | 1497.09 | 1395.39 | 1487.69 | 1471.99 | 1479.79 | 1531.89 | 1526.69 | 1303.79 | 1343.69 | 1540.29 | 1804.99 | 1751.95 | 1721.09 | 1548.37 | 1442.59 | 1340.09 | 1146.19 | 1242.69
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 7
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/7 |  |  | 2080/10/7 |  |  | Monday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 606.3 | 563.5 | 590.5 | 547.6 | 567.7 | 573.3 | 573.7 | 512.4 | 414.6 | 405.2 | 395.7 | 376.2 | 475 | 527.6 | 605.3 | 581.3 | 631.6 | 627.2 | 638 | 545.6 | 619.8 | 554.2 | 451.1 | 413.1 | 421.9 | 424.6 | 527.5 | 605.4 | 622.5 | 652.5 | 571
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1641MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1161 | 1168.79 | 1204.09 | 1161.29 | 1188.99 | 1162.39 | 1230.19 | 1267.09 | 1342.39 | 1446.29 | 1550.09 | 1641.49 | 1618.49 | 1593.69 | 1605.09 | 1556.09 | 1413.59 | 1400.09 | 1443.99 | 1484.19 | 1451.59 | 1380.39 | 1483.69 | 1662.39 | 1805.65 | 1778.65 | 1695.09 | 1633.89 | 1592.29 | 1361.59 | 1306.59 | 1274.29
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 29.5 | 29.5 | 29.5 | 29 | 29.2 | 86 | 29.5 | 27
Likhu-II(55) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 9.9 | 9.9
Super Dordi (54) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 13.1 | 13.1 | 54 | 13.1 | 10.2
Likhu-IV(52.4) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 16.1 | 16.6 | 52.4 | 16.6 | 15.4
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.8 | 28.8 | 28.8 | 28.7 | 28.8 | 50 | 28.8 | 28.7
Upper Bhotekoshi Khola(45) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 17.2 | 17.2 | 17.2 | 16.9 | 16.9 | 45 | 17.2 | 16.6
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16
Mistri Khola(42) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 7.9 | 7.9 | 30 | 8.4 | 7.9
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 7.9 | 28 | 8.2 | 7.9
Dordi(27) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 8 | 7.7 | 30 | 8 | 6.4
Upper Madi(25) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 9.5 | 8.7 | 25 | 9.5 | 6.5
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 8.4 | 8.4 | 25 | 8.4 | 7.2
Solu Khola(23.5) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.7 | 7.7 | 23.5 | 7.7 | 7.6
Upper Chaku A(22.2) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 4.5 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.3 | 10.7 | 22 | 10.7 | 10.3
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 0.91667: 25.8; 0.95833: 25.6 | 240 | 25.8 | 25.6
Total IPP | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 479.45 | 483.15 | 483.15 | 483.15 | 491.15 | 490.95 | 1042.4 | 491.15 | 479.45
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 50 | 200 | 140 | 190 | 220 | 200 | 140 | 70 | 50 | 70 | 70 | 140 | 100 | 50 | 30 | 100 | 220 | 220 | 160 | 160 | 60 | 15 | 0 | 0 | 456 | 220 | 0
Khimti Khola(60) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 60 | 28 | 28
Chilime(22.1) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 9 | 9.1 | 9 | 9 | 8.4 | 8.3 | 8.2 | 8.2 | 8.1 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 15.1 | 15.2 | 9.1 | 9 | 9.1 | 22.1 | 15.2 | 8.1
Total NEA SUBSIDIARIES | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 63.2 | 63.2 | 87 | 237.1 | 177 | 227 | 256.4 | 236.3 | 176.2 | 106.2 | 86.1 | 106.2 | 106.2 | 176.2 | 136.2 | 86.2 | 66.2 | 136.2 | 256.2 | 256.2 | 196.2 | 203.1 | 103.2 | 52.1 | 37 | 37.1 | 538.1 | 256.4 | 37
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 32.8 | 60.8 | 60.9 | 93.1 | 93.1 | 93.1 | 97.3 | 97.8 | 97.5 | 61.2 | 60.9 | 60.9 | 60.9 | 60.9 | 60.9 | 60.9 | 87 | 142.1 | 142.1 | 131.7 | 92.2 | 61.9 | 61.1 | 0 | 0 | 144 | 142.1 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 55 | 35 | 35 | 0 | 0 | 0 | 50 | 60 | 45 | 24.6 | 24.6 | 24.6 | 25 | 0 | 70 | 60 | 0
MRS(69) | 0 | 0 | 0 | 0 | 16.3 | 38 | 36.5 | 36.6 | 36.6 | 35.8 | 35.8 | 35.8 | 46.1 | 46.8 | 33.7 | 31.9 | 22.9 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | 59.8 | 68.1 | 68.1 | 68.1 | 69.5 | 60 | 52.5 | 35.5 | 0 | 69 | 69.5 | 0
U Trisuli 3A(60) | 37.3 | 37.3 | 37.3 | 38 | 38 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.8 | 38.3 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 38 | 30 | 30.2 | 31 | 42.1 | 40.1 | 60 | 42.1 | 30
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 23 | 23 | 23 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 10 | 10 | 15 | 28 | 28 | 23 | 15 | 10 | 10 | 10 | 10 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 1.1 | 5 | 5.3 | 11 | 12.3 | 14.1 | 13.8 | 13.8 | 8.4 | 5 | 1.2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14.1 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.9 | 10 | 14.1 | 10 | 9.8
MODI(14) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 4.9 | 5.1 | 14 | 5.1 | 0
SUN(10.05) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10.05 | 4 | 4
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 4.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.54
Total ROR | 75.64 | 75.64 | 75.64 | 76.34 | 92.64 | 115.34 | 146.64 | 197.74 | 212.84 | 274.54 | 275.34 | 282.44 | 297.24 | 289.94 | 278.34 | 242.74 | 233.14 | 226.74 | 201.34 | 197.94 | 169.14 | 168.24 | 242.54 | 368.9 | 379.9 | 347.54 | 273.04 | 228.44 | 220.94 | 155.94 | 93.74 | 489.91 | 379.9 | 75.64
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 66 | 62.7 | 66.9 | 66.5 | 65.6 | 59.3 | 56.5 | 67.9 | 74.2 | 67.4 | 65 | 62 | 64 | 61.8 | 60.2 | 55 | 55.2 | 55.5 | 58 | 70 | 60.5 | 68.7 | 70.5 | 67.1 | 68.6 | 71.9 | 65.6 | 61 | 56 | 64 | 63.5 |  | 74.2 | 55
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 392 | 420 | 394 | 400 | 390 | 396 | 408 | 380 | 264 | 234 | 226 | 230 | 260 | 352 | 406 | 390 | 366 | 402 | 390 | 400 | 380 | 409.1 | 383 | 271 | 237 | 244 | 246.8 | 349.7 | 390.4 | 388.9 | 402.5 |  | 420 | 226
RAMNAGAR | [32 empty] | 0 | 0
RAXAUL 132 | 113 | 123.6 | 102.6 | 124 | 92 | 112.4 | 108.8 | 125.8 | 120.2 | 56.2 | 56.2 | 52 | 0 | 0 | 0 | 98 | 97 | 102 | 105 | 99 | 56 | 46 | 49 | 56 | 52 | 53 | 61 | 64.6 | 100 | 104 | 124 |  | 125.8 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 57 | 58 | 51.7 | 52.2 | 61.2 | 61.4 | 62.3 | 63.1 | 72.1 | 74.2 | 69 | 49.1 | 96 | 51.7 | 57 | 55.5 | 53 | 51.2 | 52.2 | 59 | 65.6 | 62.5 |  | 96 | 0
Total IMPORT | 571 | 606.3 | 563.5 | 590.5 | 547.6 | 567.7 | 573.3 | 573.7 | 512.4 | 414.6 | 405.2 | 395.7 | 376.2 | 475 | 527.6 | 605.3 | 581.3 | 631.6 | 627.2 | 638 | 545.6 | 619.8 | 554.2 | 451.1 | 413.1 | 421.9 | 424.6 | 527.5 | 605.4 | 622.5 | 652.5 | 0 | 652.5 | 376.2
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1168.79 | 1204.09 | 1161.29 | 1188.99 | 1162.39 | 1230.19 | 1267.09 | 1342.39 | 1446.29 | 1350.09 | 1391.49 | 1418.49 | 1393.69 | 1425.09 | 1396.09 | 1413.59 | 1400.09 | 1443.99 | 1484.19 | 1451.59 | 1280.39 | 1333.69 | 1412.39 | 1555.65 | 1528.65 | 1445.09 | 1383.89 | 1342.29 | 1361.59 | 1306.59 | 1274.29 | 2231.81 | 1555.65 | 1161.29
Interruption/Tripping | 0: 0; 0.041667: 0; 0.083333: 0; 0.25: 0; 0.29167: 200; 0.3125: 250; 0.33333: 200; 0.375: 200; 0.41667: 180; 0.45833: 160; 0.70833: 100; 0.72917: 150; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 250 |  | 250 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1168.79 | 1204.09 | 1161.29 | 1188.99 | 1162.39 | 1230.19 | 1267.09 | 1342.39 | 1446.29 | 1550.09 | 1641.49 | 1618.49 | 1593.69 | 1605.09 | 1556.09 | 1413.59 | 1400.09 | 1443.99 | 1484.19 | 1451.59 | 1380.39 | 1483.69 | 1662.39 | 1805.65 | 1778.65 | 1695.09 | 1633.89 | 1592.29 | 1361.59 | 1306.59 | 1274.29 | 1693.71 | 1805.65 | 1161.29
TOTAL NATIONAL LOAD (ACTUAL) | 1168.79 | 1204.09 | 1161.29 | 1188.99 | 1162.39 | 1230.19 | 1267.09 | 1342.39 | 1446.29 | 1550.09 | 1641.49 | 1618.49 | 1593.69 | 1605.09 | 1556.09 | 1413.59 | 1400.09 | 1443.99 | 1484.19 | 1451.59 | 1380.39 | 1483.69 | 1662.39 | 1805.65 | 1778.65 | 1695.09 | 1633.89 | 1592.29 | 1361.59 | 1306.59 | 1274.29 |  | 1805.65 | 1161.29
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
NET IMPORT | 571 | 606.3 | 563.5 | 590.5 | 547.6 | 567.7 | 573.3 | 573.7 | 512.4 | 414.6 | 405.2 | 395.7 | 376.2 | 475 | 527.6 | 605.3 | 581.3 | 631.6 | 627.2 | 638 | 545.6 | 619.8 | 554.2 | 451.1 | 413.1 | 421.9 | 424.6 | 527.5 | 605.4 | 622.5 | 652.5 |  | 652.5 | 376.2
HZ | 50.01 | 49.94 | 50.06 | 50.03 | 50.056 | 50.024 | 50.012 | 49.92 | 50.105 | 50.052 |  | 50.314 | 50.064 | 50.187 | 50.102 | 49.981 | 49.962 | 49.993 | 49.915 | 49.93 | 49.998 | 49.883 | 50.032 | 49.923 | 49.935 | 50.044 | 50.114 | 50.02 | 50.073 | 50.02 | 50.01 |  | 50.314 | 49.883
HTD 132KV | 129.4 | 127.6 | 128.6 | 129.2 | 128.8 | 128 | 129.6 | 127.5 | 126.7 | 129.3 |  | 125.3 | 123.7 | 124.6 | 122 | 125.3 | 126.1 | 125.3 | 123.7 | 125 | 129 | 127 | 127.4 | 125.6 | 126.8 | 128.4 | 129.9 | 130.4 | 129.2 | 130 | 127.9 |  | 130.4 | 122
SUI 132KV | 132.4 | 131.2 | 131.9 | 132.5 | 132.3 | 131.6 | 132.4 | 130 | 129.3 | 130.4 |  | 126.8 | 125.8 | 126.9 | 124.9 | 127.5 | 128.2 | 127.6 | 126.1 | 127 | 130.7 | 128.7 | 129 | 127 | 127.8 | 129.3 | 130.9 | 131.6 | 131.1 | 132.6 | 131.1 |  | 132.6 | 124.9
DUBI 132KV | 0.91667: 131.9; 0.95833: 127.9 |  | 131.9 | 127.9
ANAMANI 132KV | 0.91667: 135; 0.95833: 131.6 |  | 135 | 131.6
KG-A 132KV | 131.1 | 130.4 | 132.4 | 133.6 | 132.9 | 131.2 | 135.4 | 132.7 | 131.8 | 135.2 |  | 131.7 | 131.2 | 132.4 | 130.3 | 133 | 134.4 | 133 | 132.5 | 134 | 136.9 | 135 | 134.9 | 133.5 | 133.6 | 135 | 137.4 | 137.6 | 137.2 | 135 | 130.4 |  | 137.6 | 130.3
KOHALPUR 132KV | 131.6 | 128.4 | 126.3 | 127.4 | 131.1 | 128.3 | 133.9 | 125.4 | 125.6 | 132 |  | 131.9 | 133.5 | 133.9 | 127.6 | 134.2 | 129.6 | 135.5 | 133.9 | 133 | 133.6 | 127.9 | 127 | 127.8 | 132.4 | 127.8 | 135.8 | 130.9 | 131.8 | 126.6 | 126.9 |  | 135.8 | 125.4
SUI 66KV | 66.5 | 66 | 66.7 | 66.7 | 66.6 | 66.1 | 66.4 | 65.3 | 64.9 | 65.5 |  | 63.6 | 63.3 | 64 | 62.5 | 64.1 | 64.5 | 64 | 63.3 | 63.7 | 65.7 | 64.6 | 64.7 | 63.5 | 64.1 | 64.8 | 65.6 | 65.9 | 65.6 | 66.4 | 66.1 |  | 66.7 | 62.5
[33 empty] | 0 | 0
Kathmandu Load | 152.54 | 141.42 | 116.22 | 135.24 | 141.482 | 162.039 | 195.572 | 237.626 | 269.008 | 312.354 | 94.24 | 376.616 | 375.917 | 366.958 | 42 | 325.596 | 309.711 | 292.84 | 295.94 | 294.64 | 299.44 | 321.44 | 343.84 | 412.2 | 411.22 | 387.18 | 356.32 | 336.06 |  | 218.14 | 164.08 |  | 412.2 | 42
MRS-SYU | -7.9 | -19.2 | -39 | -16.9 | -17 | -11 | -3 | 5.5 | 15 | 28.5 |  | 26.2 | 29.9 | 34.3 | 31.4 | 23.4 | 20.3 | 15.5 | 14 | 14 | 13.4 | 13 | 26 | 45 | 48 | 48.1 | 38.6 | 31.9 | 33.1 | 1.9 | -14.7 | 75 | 48.1 | -39
NMRS-MATA | -14.5 | -27.1 | -26.8 | -25.2 | -26.7 | -21 | -9 | 4 | 15.5 | 41.5 |  | 38.1 | 43.5 | 49.1 | 39.9 | 27.3 | 24.4 | 18.1 | 14 | 14 | 17.6 | 17.1 | 34.2 | 60 | 64.5 | 64.6 | 50.4 | 41.8 | 36 | -4.6 | -24.9 | 240 | 64.6 | -27.1
KL2-MATA | -12.5 | -14 | -16 | -17.2 | -15.9 | -14.5 | -6.9 | 0 | 5.3 | 20.3 |  | 37 | 27.9 | 19.5 | 6.5 | 21.5 | 17.2 | 14 | 13 | 17 | 32 | 37 | 37 | 47 | 43 | 41 | 37.9 | 36.2 | 24 | 6.6 | -2.8 | 240 | 47 | -17.2
KL1-SYU | -8 | -10.2 | -9.9 | -11.7 | -10.7 | -10.6 | -3.2 | 1 | 3.8 | 18.1 |  | 22.2 | 20.7 | 18.5 | 10 | 10.6 | 9.6 | 8.4 | 4.3 | 6 | 17 | 18.2 | 22 | 27 | 27 | 26.8 | 23.5 | 22.5 | 10.6 | -0.3 | -7.6 | 60 | 27 | -11.7
KHIMTI-LAMOSANGHU | 104 | 120.48 | 116.48 | 114.1 | 119.642 | 125.999 | 124.532 | 133.986 | 136.268 | 110.514 |  | 154.976 | 155.477 | 142.618 | 145.796 | 140.056 | 135.771 | 134.4 | 153.6 | 150 | 129.6 | 147.2 | 136 | 139.2 | 134.72 | 119.04 | 126.28 | 123.82 | 119.72 | 123.2 | 124.64 | 120 | 155.477 | 104
LAMOSHANGU-BHAKTAPUR | 76.9 | 83.6 | 83.3 | 82.4 | 83.9 | 88.9 | 86.4 | 90.9 | 91.9 | 78.2 |  | 99.4 | 99.6 | 93 | 98.1 | 91.3 | 88.7 | 92 | 103 | 102 | 89 | 98 | 93 | 93 | 92 | 84 | 87 | 85.7 | 83.7 | 86.4 | 88.8
BALAJU-SYUCHATAR | 60.5 | 80 | 80 | 78 | 75 | 73.8 | 55.2 | 42.2 | 26.7 | -15.6 |  | -8.1 | -6.4 | -7.1 | 17.63 | 12.63 | 18.6 | 25 | 40 | 38 | 11 | 12 | -12 | -43 | -43 | -43.2 | -24.7 | -16.3 | -3.6 | 42.8 | 61.2
DHALKE-NAWALPUR I | 73.3 | 83.4 | 80.2 | 80.6 | 80.2 | 90.5 | 84.9 | 87.6 | 80.8 | 67.8 |  | 89.2 | 95.3 | 93.2 | 112.6 | 85.1 | 82.9 | 85 | 97 | 96 | 83 | 92 | 85 | 82 | 69 | 62.4 | 67.2 | 74.2 | 74.4 | 82.6 | 83.2 |  | 112.6 | 62.4
N. BHARATPUR-BARDGHAT I | 23.4 | 32.8 | 32.7 | 31.2 | 30.6 | 34.5 | 25.5 | 20.7 | 9.2 | 1.3 |  | 1.6 | 1 | 0 | 0 | 8.8 | 7.9 | 7 | 8.1 | 6 | 1 | 1.5 | 0 | -9 | -9 | -8 | -2.4 | 2.5 | 1.3 | 15.2 | 25.1 |  | 34.5 | -9
DAMAK-DUHABI | 0.91667: -10.7; 0.95833: -5.3 |  | -5.3 | -10.7
HETAUDA-KAMANE | 19.3 | 21.2 | 21.2 | 21.4 | 21.5 | 22.5 | 23.1 | 22 | 23 | 12.1 |  | 13.8 | 14.2 | 13.2 | 13.3 | 21.2 | 20.7 | 27 | 27 | 25 | 12 | 12 | 12.1 | 13 | 13 | 11 | 9.9 | 10.1 | 11.8 | 10.1 | 9.7 |  | 27 | 9.7
MIRCHAIYA LAHAN 2 | 95.6 | 92.8 | 90.5 | 96.6 | 93.2 | 89.8 | 95.9 | 95.8 | 102.8 | 99.2 |  | 98.2 | 95 | 110.3 | 108.5 | 113 | 107.5 | 109 | 117 | 114 | 95.1 | 84 | 110 | 115 | 106 | 97 | 92.3 | 91.4 | 94.9 | 90 | 89.2 |  | 117 | 84
Water Level
UTK | 1984.8 | 1985.02 | 1985.25 | 1985.47 | 1985.69 | 1985.9 |  | 1986 |  | 1985.78 |  | 1985.4 | 1985.1 | 1984.72 | 1984.62 | 1984.68 | 1984.73 | 1984.7 | 1984.62 | 1984.45 | 1984.42 | 1984.49 |  |  | 1984.15 |  | 1983.85 |  | 1983.85 | 1984.07 | 1984.32
KGA | 521.37 | 521.7 | 522.04 | 522.41 | 522.67 | 522.96 |  | 523.08 |  | 522.98 |  | 522.78 | 522.59 | 522.4 | 522.14 | 522 | 521.96 | 521.96 |  | 521.92 | 521.88 | 521.87 | 521.84 |  | 521.44 |  | 521 |  | 520.85 | 520.93 | 521.36
MMRS | 622.88 | 623.24 | 623.54 | 623..93 | 624.33 | 624.66 |  | 624.91 |  | 624.91 |  | 624.7 | 624.51 | 624.31 | 624.08 | 623.84 | 623.55 | 623.04 |  | 622.81 | 622.83 | 623.1 | 623.24 |  | 622.96 |  | 622.66 |  | 622.75 | 622.75 | 623.16
MRS | 336.04 | 336.54 | 336.86 | 337.06 | 337.26 | 337.29 |  | 337.16 |  | 336.99 |  | 336.8 | 336.63 | 336.31 | 335.98 | 335.75 | 335.56 | 335.66 |  | 336.23 | 336.5 | 336.67 | 336.81 |  | 336.8 |  | 336.48 |  | 336.24 | 336.11 | 336.15
CHM | 884 | 884.6 | 885.3 | 885.7 | 886.4 | 886 |  | 887.2 |  | 887 |  | 886.1 | 885.2 | 884.9 | 884.8 | 884.7 | 884.5 | 885 | 885.3 | 886 | 885.9 | 885.9 | 885.8 |  | 884.8 |  | 884 |  |  |  | 883.8
KL 1 | 0: 1519.12; 0.33333: 1519.13; 0.54167: 1519.14
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1641.49; 0.041667: 7:30
7
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/7); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/7)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1168.79; 0.66667: 1204.09; 0.70833: 1161.29; 0.72917: 1188.99; 0.75: 1162.39; 0.77083: 1230.19; 0.79167: 1267.09; 0.8125: 1342.39; 0.83333: 1446.29; 0.85417: 1550.09; 0.875: 1641.49; 0.91667: 1618.49; 0.95833: 1593.69 | 1605.09 | 1556.09 | 1413.59 | 1400.09 | 1443.99 | 1484.19 | 1451.59 | 1380.39 | 1483.69 | 1662.39 | 1805.65 | 1778.65 | 1695.09 | 1633.89 | 1592.29 | 1361.59 | 1306.59 | 1274.29
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 8
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/8 |  |  | 2080/10/8 |  |  | Tuesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 562.1 | 551.3 | 540.9 | 572.8 | 599 | 602 | 586 | 555 | 475.8 | 358.8 | 349.9 | 388.5 | 538.2 | 628.2 | 645.4 | 617 | 644.4 | 642.6 | 622.5 | 549.1 | 574.7 | 422 | 372 | 344.5 | 371.1 | 374 | 421 | 484 | 541 | 539 | 572.5
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1678MW at 7:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1148 | 1183.09 | 1172.69 | 1160.19 | 1147.99 | 1179.49 | 1269.29 | 1295.52 | 1385.89 | 1508.49 | 1678.29 | 1619.99 | 1635.59 | 1515.89 | 1494.19 | 1585.09 | 1510.19 | 1442.79 | 1455.19 | 1489.59 | 1459.79 | 1606.29 | 1559.79 | 1686.59 | 1822.65 | 1781.25 | 1775.89 | 1603.79 | 1494.79 | 1288.79 | 1315.79 | 1265.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 29.2 | 29.5 | 29.9 | 29.1 | 28.8 | 29.2 | 29.1 | 29.1 | 29.2 | 29.1 | 29.2 | 29.2 | 28.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 28.4 | 26.6 | 26.6 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 86 | 29.9 | 25
Likhu-II(55) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 9.9
Super Dordi (54) | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 54 | 12 | 11
Likhu-IV(52.4) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 52.4 | 16.6 | 13.2
Upper Marsyangdi "A"(50) | 29.2 | 28.9 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 30.3 | 30.3 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 50 | 30.3 | 28.9
Upper Bhotekoshi Khola(45) | 16.9 | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 15.1 | 15.1 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 45 | 16.9 | 15.1
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16
Mistri Khola(42) | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 42 | 8 | 7
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 38.46 | 12.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 24 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 24 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.1 | 8.1 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 30 | 8.8 | 8.1
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24.2 | 9 | 9
Lower Likhu(28) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 | 9 | 9
Dordi(27) | 6.6 | 6.2 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 30 | 7.3 | 6.2
Upper Madi(25) | 8.7 | 8.7 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 25 | 8.7 | 8.4
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.9 | 7.9 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 25 | 7.9 | 7.5
Solu Khola(23.5) | 7.2 | 7.2 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 23.5 | 7.3 | 7.2
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 0 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 11.8 | 12.4 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 22 | 12.4 | 11.8
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 25.9 | 26 | 25.3 | 24.4 | 25.3 | 27.9 | 27.2 | 26.5 | 25.4 | 23.4 | 21.4 | 21.4 | 21.4 | 15.6 | 20 | 20 | 19.8 | 19.8 | 22.5 | 22.5 | 22.5 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 240 | 27.9 | 15.6
Total IPP | 490.55 | 490.75 | 490.55 | 489.75 | 489.45 | 489.85 | 489.75 | 489.75 | 489.85 | 489.75 | 489.85 | 489.85 | 488.85 | 487.85 | 487.85 | 487.85 | 487.85 | 487.85 | 487.85 | 487.85 | 505.25 | 484.25 | 484.25 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 483.95 | 1042.4 | 505.25 | 483.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 110 | 160 | 200 | 100 | 30 | 75 | 75 | 40 | 40 | 76 | 76 | 30 | 30 | 220 | 270 | 280 | 280 | 150 | 100 | 30 | 0 | 0 | 456 | 280 | 0
Khimti Khola(60) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 28 | 27
Chilime(22.1) | 8.6 | 8.5 | 8.5 | 8.5 | 8.4 | 8.4 | 8.63 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.8 | 8.4 | 8.4 | 0 | 7.8 | 7.4 | 7.4 | 7.4 | 7.4 | 12.4 | 12.4 | 12 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 22.1 | 12.4 | 0
Total NEA SUBSIDIARIES | 36.6 | 36.5 | 36.5 | 36.5 | 36.4 | 36.4 | 36.63 | 36.6 | 136.6 | 146.6 | 196.6 | 235.6 | 135.8 | 65.4 | 110.4 | 102 | 74.8 | 74.4 | 110.4 | 110.4 | 64.4 | 69.4 | 259.4 | 309 | 319.4 | 319.4 | 189.4 | 139.4 | 69.4 | 39.4 | 39.4 | 538.1 | 319.4 | 36.4
KGA(144) | 0 | 0 | 0 | 0 | 0 | 30 | 31.7 | 95 | 116 | 121 | 101 | 93.7 | 71.5 | 71.5 | 66.7 | 70.7 | 61.7 | 62.1 | 62.1 | 62.1 | 62.1 | 63.1 | 97 | 142 | 122 | 122 | 97 | 60 | 61 | 61 | 30 | 144 | 142 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 50 | 50 | 45 | 35 | 35 | 45 | 45 | 45 | 30 | 30 | 25 | 25 | 25 | 35 | 70 | 70 | 70 | 50 | 45 | 45 | 45 | 35 | 70 | 70 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 35 | 46.4 | 52.5 | 60 | 53.3 | 51 | 50.8 | 50.5 | 50.5 | 50.2 | 49.5 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 0 | 16 | 53 | 53 | 53 | 53 | 52 | 52 | 52 | 40 | 69 | 60 | 0
U Trisuli 3A(60) | 40.1 | 40.1 | 40.1 | 39.1 | 39.1 | 37.3 | 37.3 | 39.3 | 39.3 | 40.1 | 40.1 | 38 | 38.3 | 38.3 | 39.3 | 40.1 | 38 | 38 | 38 | 38 | 38 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 60 | 40.1 | 37.3
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 10 | 10 | 23 | 23 | 23 | 23 | 10 | 10 | 10 | 15 | 30 | 23 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 1.2 | 5.9 | 5.9 | 5.9 | 16 | 15.5 | 15.5 | 10.7 | 6 | 4.5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 14.1 | 10 | 9.8
MODI(14) | 4.8 | 4.8 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 14 | 5.3 | 3.2
SUN(10.05) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5
Total ROR | 83.44 | 83.34 | 81.84 | 80.84 | 80.84 | 144.04 | 167.14 | 273.54 | 327.04 | 316.14 | 294.74 | 280.24 | 252.74 | 252.74 | 258.64 | 274.94 | 263.14 | 248.54 | 248.74 | 239.04 | 237.54 | 181.44 | 240.94 | 371.4 | 353.4 | 351.44 | 306.44 | 250.44 | 251.44 | 251.44 | 203.44 | 489.91 | 371.4 | 80.84
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | 0.77083: 4.7 | 32 | 4.7 | 4.7
KL3(14) | 0.77083: 1.6 | 14 | 1.6 | 1.6
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 6.3 | 0
TANAKPUR | 61.3 | 58.9 | 62.8 | 60 | 51.8 | 69 | 58 | 70 | 65 | 57.6 | 59.6 | 60 | 61 | 71.1 | 60.7 | 69.2 | 63.3 | 53.3 | 66 | 59.5 | 61 | 62.4 | 62 | 66 | 60.5 | 57.7 | 58 | 64 | 62 | 72 | 70 |  | 72 | 51.8
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 386.2 | 391.2 | 378.5 | 374.9 | 397 | 415 | 439 | 418 | 310 | 279 | 190.5 | 187 | 259 | 345.3 | 406 | 394.2 | 376 | 422 | 404 | 409 | 392 | 440 | 309 | 240 | 220 | 249 | 255 | 295 | 357 | 398 | 399 |  | 440 | 187
RAMNAGAR | [32 empty] | 0 | 0
RAXAUL 132 | 125 | 112 | 110 | 106 | 124 | 115 | 105 | 98 | 102 | 60 | 36.4 | 32 | 0 | 46 | 85 | 104 | 111 | 105 | 102.6 | 84 | 52.6 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 125 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 0 | 0 | 0 | [5 empty] | 78 | 79.2 | 72.3 | 70.9 | 68.5 | 75.8 | 76.5 | 78 | 66.7 | 64.1 | 70 | 70 | 43.5 | 42.1 | 51 | 66 | 64 | 64.4 | 61 | 62 | 65 | 71 | 70 |  | 79.2 | 0
Total IMPORT | 572.5 | 562.1 | 551.3 | 540.9 | 572.8 | 599 | 602 | 586 | 555 | 475.8 | 358.8 | 349.9 | 388.5 | 538.2 | 628.2 | 645.4 | 617 | 644.4 | 642.6 | 622.5 | 549.1 | 574.7 | 422 | 372 | 344.5 | 371.1 | 374 | 421 | 484 | 541 | 539 | 0 | 645.4 | 344.5
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1183.09 | 1172.69 | 1160.19 | 1147.99 | 1179.49 | 1269.29 | 1295.52 | 1385.89 | 1508.49 | 1428.29 | 1339.99 | 1355.59 | 1265.89 | 1344.19 | 1485.09 | 1510.19 | 1442.79 | 1455.19 | 1489.59 | 1459.79 | 1356.29 | 1309.79 | 1406.59 | 1542.65 | 1501.25 | 1525.89 | 1353.79 | 1294.79 | 1288.79 | 1315.79 | 1265.79 | 2231.81 | 1542.65 | 1147.99
Interruption/Tripping | 0.29167: 250; 0.3125: 280; 0.33333: 280; 0.375: 250; 0.41667: 150; 0.45833: 100; 0.70833: 250; 0.72917: 250; 0.75: 280; 0.77083: 280; 0.79167: 280; 0.8125: 250; 0.83333: 250; 0.85417: 200; 0.875: 0; 0.91667: 0; 0.95833: 0 |  | 280 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1183.09 | 1172.69 | 1160.19 | 1147.99 | 1179.49 | 1269.29 | 1295.52 | 1385.89 | 1508.49 | 1678.29 | 1619.99 | 1635.59 | 1515.89 | 1494.19 | 1585.09 | 1510.19 | 1442.79 | 1455.19 | 1489.59 | 1459.79 | 1606.29 | 1559.79 | 1686.59 | 1822.65 | 1781.25 | 1775.89 | 1603.79 | 1494.79 | 1288.79 | 1315.79 | 1265.79 | 1693.71 | 1822.65 | 1147.99
TOTAL NATIONAL LOAD (ACTUAL) | 1183.09 | 1172.69 | 1160.19 | 1147.99 | 1179.49 | 1269.29 | 1295.52 | 1385.89 | 1508.49 | 1678.29 | 1619.99 | 1635.59 | 1515.89 | 1494.19 | 1585.09 | 1510.19 | 1442.79 | 1455.19 | 1489.59 | 1459.79 | 1606.29 | 1559.79 | 1686.59 | 1822.65 | 1781.25 | 1775.89 | 1603.79 | 1494.79 | 1288.79 | 1315.79 | 1265.79 |  | 1822.65 | 1147.99
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
NET IMPORT | 572.5 | 562.1 | 551.3 | 540.9 | 572.8 | 599 | 602 | 586 | 555 | 475.8 | 358.8 | 349.9 | 388.5 | 538.2 | 628.2 | 645.4 | 617 | 644.4 | 642.6 | 622.5 | 549.1 | 574.7 | 422 | 372 | 344.5 | 371.1 | 374 | 421 | 484 | 541 | 539 |  | 645.4 | 344.5
HZ | 49.97 | 50 | 49.97 | 50.075 | 49.986 | 49.936 | 49.97 | 50.046 | 49.965 | 50.072 | 49.813 | 50.038 | 49.986 | 49.974 | 49.959 | 49.855 | 49.832 | 50.026 | 49.941 | 49.915 | 49.964 | 50.027 | 49.885 | 49.845 | 49.627 | 49.923 | 50.1 | 50.04 | 50.01 | 50.01 | 49.95 |  | 50.1 | 49.627
HTD 132KV | 129.7 | 127.8 | 129.4 | 128.7 | 127.7 | 127.9 | 127.3 | 126.8 | 127.5 | 128.5 | 126.5 | 127 | 126.3 | 126.8 | 123.6 | 124.6 | 125.8 | 124.2 | 124.4 | 124.1 | 128.5 | 126.8 | 125.4 | 126.4 | 127.2 | 127.9 | 130 | 130 | 130 | 128 | 128 |  | 130 | 123.6
SUI 132KV | 133.1 | 132.1 | 132.7 | 132.3 | 131.7 | 131.4 | 130.8 | 130.1 | 129.9 | 130 | 127.7 | 127.7 | 128 | 128.1 | 125.7 | 126.6 | 128.2 | 126.6 | 126.5 | 126.4 | 129.9 | 128.5 | 126.9 | 127.2 | 128 | 129 | 131 | 131.4 | 131.4 | 131 | 131 |  | 133.1 | 125.7
DUBI 132KV | 131.3 | 129.1 | 131.5 | 131.6 | 130.2 | 127.1 | 128 | 127.4 | 125.9 | 129.7 | 129.7 | 128.8 | 130.9 | 128.4 | 120.6 | 127 | 127.5 | 124.2 | 128.4 | 127.8 | 129.9 | 127 | 1278 | 130.2 | 131.6 | 131 | 133 | 132 | 132 | 129 | 129 |  | 1278 | 120.6
ANAMANI 132KV | 133.1 | 131.2 | 133.1 | 133.3 | 131.8 | 130.8 | 131.8 | 129.1 | 128.8 | 130.6 | 129.5 | 128.6 | 131.9 | 130 | 123.4 | 130 | 131.1 | 128.9 | 130.6 | 129.2 | 131.5 | 128.1 | 126.1 | 129.4 | 131.4 | 132.8 | 133 | 132.5 | 132 | 130 | 131 |  | 133.3 | 123.4
KG-A 132KV | 131.4 | 130.6 | 132.3 | 131.5 | 130.6 | 132 | 131.9 | 134 | 134.3 | 135.5 | 135.5 | 135.6 | 134.7 | 134.7 | 131.2 | 131.6 | 132.6 | 131.6 | 130.5 | 130.6 | 134.7 | 134.3 | 133.2 | 135.3 | 136.4 | 136.2 | 137 | 137 | 137 | 134 | 134 |  | 137 | 130.5
KOHALPUR 132KV | 133 | 133.8 | 130.7 | 132.8 | 136.1 | 131.6 | 131.5 | 125.9 | 127.1 | 133.1 | 129 | 131.8 | 130.2 | 133.8 | 133.6 | 130.1 | 136.4 | 135.3 | 135.8 | 133 | 133.6 | 130.6 | 132.9 | 129 | 135.5 | 135.7 | 136 | 133.6 | 135 | 130 | 130 |  | 136.4 | 125.9
SUI 66KV | 67.1 | 66.5 | 66.9 | 66.7 | 66.5 | 66.2 | 66 | 65.7 | 65 | 65.3 | 63.8 | 63.9 | 64 | 63.9 | 62.5 | 63.1 | 64 | 63.3 | 63.4 | 63 | 65.1 | 64.2 | 63.4 | 63.8 | 64.1 | 64.8 | 65.8 | 65.8 | 65.8 | 65.8 | 66 |  | 67.1 | 62.5
[33 empty] | 0 | 0
Kathmandu Load | 140.22 | 135.86 | 127.74 | 131.116 | 146.2 | 190.6 | 194.62 | 261.3 | 302.6 | 274.06 | 375.52 | 378.812 | 353.219 | 357.971 | 42 | 338.613 | 299.841 | 298.948 | 305.64 | 287.04 | 311.504 | 314.344 | 345.74 | 422.6 | 425.5 | 401.54 | 371.84 | 341.14 | 295.34 | 223.84 | 183.84 |  | 425.5 | 42
MRS-SYU | -18.3 | -19 | -19.2 | -20 | -20 | -5.5 | -5.1 | 15.5 | 40.6 | 37.2 | 36.2 | 36.8 | 36.4 | 38.4 | 34.8 | 33.9 | 32.5 | 27.3 | 23 | 16.1 | 20.7 | 11.4 | 21.7 | 43.3 | 40.5 | 38.4 | 39 | 34.5 | 35 | 32 | 18 | 75 | 43.3 | -20
NMRS-MATA | -28.9 | -30.9 | -29.9 | -32 | -32 | -15.1 | -14.6 | 13.3 | 48.9 | 51 | 48.1 | 49.5 | 48 | 52.2 | 43.2 | 40.2 | 38.2 | 29.7 | 24.5 | 19 | 27.3 | 13.5 | 30.7 | 59.6 | 55.4 | 52 | 53 | 46.8 | 45 | 39 | 20 | 240 | 59.6 | -32
KL2-MATA | -8.3 | -13.6 | -16.7 | -14.2 | -11.2 | -3.8 | -3.4 | 7.2 | 10.3 | -28 | 41.7 | 43.3 | 31 | 35 | 23 | 15.8 | 6 | 6.2 | 12.5 | 13 | 27.9 | 35.6 | 33 | 44 | 45 | 40 | 36 | 28 | 20 | -22 | -31 | 240 | 45 | -31
KL1-SYU | -4.8 | -8.9 | -10 | -7.9 | -9.1 | -1.7 | -3.9 | 6.6 | 8.7 | 20.6 | 24.2 | 24 | 20.8 | 22.7 | 7.7 | 6.1 | 2.5 | 1.8 | 7.2 | 10.2 | 20.2 | 19.1 | 21.3 | 26 | 26.9 | 26.3 | 24 | 22 | 5.5 | 0 | -3 | 60 | 26.9 | -10
KHIMTI-LAMOSANGHU | 110.88 | 118.72 | 113.6 | 116.276 | 129.56 | 129.56 | 134.48 | 129.56 | 104.96 | 103.32 | 134.48 | 136.272 | 123.079 | 115.731 | 139.779 | 136.773 | 117.401 | 130.708 | 140 | 135 | 123.164 | 145.304 | 150 | 152 | 160 | 155 | 130 | 120 | 100 | 85 | 90 | 120 | 160 | 85
LAMOSHANGU-BHAKTAPUR | 82 | 86.4 | 82.9 | 84.1 | 88.1 | 90 | 92 | 88.3 | 74.3 | 76.1 | 91 | 90.4 | 84.9 | 81.2 | 92.2 | 89.8 | 81.2 | 88.7 | 93.5 | 98.4 | 83.5 | 94.7 | 102 | 98.7 | 100 | 97 | 86 | 83 | 81 | 75 | 72
BALAJU-SYUCHATAR | 66.3 | 74.5 | 73.7 | 78 | 78 | 62.1 | 62.2 | 27.6 | -16.3 | -36.6 | -31.2 | -31 | 30.4 | -27.3 | 5.5 | 11.4 | 15.1 | 25.7 | 31.9 | 34 | 1.4 | 13.2 | 5 | -33 | -30 | -27 | -29 | -20 | -13 | 16 | 41
DHALKE-NAWALPUR I | 81.4 | 84.6 | 78.9 | 82.5 | 87 | 90.5 | 92.5 | 83.9 | 57.4 | 59.1 | 67.7 | 71 | 62.5 | 85.6 | 79 | 79 | 72.8 | 75 | 85.3 | 94 | 72.54 | 90 | 93 | 98 | 84.7 | 80 | 76 | 72 | 77 | 84 | 84 |  | 98 | 57.4
N. BHARATPUR-BARDGHAT I | 28 | 28.4 | 27.2 | 28.2 | 27.6 | 25 | 24.7 | 12.9 | -5.9 | -7.8 | -6.7 | -6.5 | -6.3 | -4.7 | 2.8 | 0 | 1.2 | 0 | 6.2 | 8.3 | 0 | 2.1 | -3.4 | -8.2 | -4.7 | -3.6 | -4 | 0 | 2 | 0 | 9 |  | 28.4 | -8.2
DAMAK-DUHABI | -4.4 | -3 | -3.8 | -4 | -3.6 | -8.9 | -9.6 | -20.1 | -29.4 | -37.1 | -42.5 | -40.9 | -24.2 | -25.5 | -24.3 | -15.9 | -15.7 | -21.8 | -17.5 | -19 | -26.6 | -36.6 | -47 | -51 | -45 | -38 | -32 | -23 | -22 | -14 | -8 |  | -3 | -51
HETAUDA-KAMANE | 9.9 | 20.5 | 22 | 22.3 | 22.3 | 23.9 | 23.8 | 23.1 | 23.2 | 11.6 | 11.9 | 12.4 | 11.3 | 11.8 | 14.3 | 19.3 | 25.3 | 26.9 | 26.2 | 27 | 10.9 | 10.8 | 10.9 | 12.3 | 12.1 | 11.1 | 10.5 | 10 | 9 | 20 | 22 |  | 27 | 9
MIRCHAIYA LAHAN 2 | 84.2 | 86.2 | 85.5 | 86.1 | 83.2 | 94.7 | 95 | 97.3 | 102.6 | 93.4 | 79.9 | 83 | 68.7 | 90.3 | 114.1 | 115.6 | 110.1 | 112.5 | 113.2 | 111 | 89.2 | 99.1 | 104 | 105 | 94 | 84 | 79 | 84 | 81 | 97 | 91 |  | 115.6 | 68.7
Water Level
UTK | 1984.55 | 1984.78 | 1985 | 1985.22 | 1985.45 | 1985.65 |  | 1985.85 |  | 1985.85 |  | 1985.65 | 1985.28 | 1985.25 | 1985.35 | 1985.32 | 1985.38 | 1985.45 | 1985.52 | 1985.5 | 1985.4 | 1985.45 | 1985.45 |  | 1984.94 |  | 1984.5 |  | 1984.42 | 1984.5
KGA | 521.59 | 521.94 | 522.26 | 522.56 | 522.84 | 523.14 |  | 523.22 |  | 522.9 |  | 522.7 | 522.59 | 522.54 | 522.5 | 522.42 | 522.36 | 522.32 | 522.29 | 522.29 | 522.15 |  | 522.06 |  | 521.69 | 521.35 | 521.35 |  | 521.225 | 521.17 | 521.21
MMRS | 623.45 | 623.88 | 624.19 | 624.58 | 624.79 | 625.16 |  | 625.36 |  | 625.03 |  | 624.9 | 624.73 | 624.55 | 624.4 | 624.11 | 623.93 | 623.87 | 623.85 | 623.84 | 623.84 |  | 623.92 |  | 623.57 |  | 623.1 |  | 622.86 |  | 622.24
MRS | 336.36 | 336.8 | 337.09 | 337.25 | 337.53 | 337.61 |  | 337.45 |  | 337.17 |  | 336.81 | 336.51 | 336.19 | 335.8 | 335.46 | 335.14 | 335.14 | 335.12 | 335.21 | 335.43 |  | 335.81 |  | 335.89 |  | 335.73 |  | 335.57 |  | 335.3
CHM | 884 | 884.8 | 885.3 | 885.9 | 886.4 | 886.9 |  | 886.9 |  | 886.8 |  | 886.8 | 886.7 | 886.6 | 886.6 | 886.6 | 886.4 | 886.4 | 886.3 | 886.3 |  |  | 885.9 |  | 885.3 |  | 884.5 |  | 884.1
KL 1 | 0.33333: 1519.17; 0.54167: 1519.18
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1678.29; 0.041667: 7:00
8
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/8); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/8)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1183.09; 0.66667: 1172.69; 0.70833: 1160.19; 0.72917: 1147.99; 0.75: 1179.49; 0.77083: 1269.29; 0.79167: 1295.52; 0.8125: 1385.89; 0.83333: 1508.49; 0.85417: 1678.29; 0.875: 1619.99; 0.91667: 1635.59; 0.95833: 1515.89 | 1494.19 | 1585.09 | 1510.19 | 1442.79 | 1455.19 | 1489.59 | 1459.79 | 1606.29 | 1559.79 | 1686.59 | 1822.65 | 1781.25 | 1775.89 | 1603.79 | 1494.79 | 1288.79 | 1315.79 | 1265.79
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 9
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/9 |  |  | 2080/10/9 |  |  | Wednesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 601 | 573.9 | 560.7 | 542.1 | 542.1 | 481.8 | 463.8 | 514 | 514 | 287 | 274.8 | 421 | 425.3 | 522 | 560.2 | 617 | 665 | 660.2 | 616.1 | 560.9 | 540 | 505.2 | 393.4 | 325.6 | 413.5 | 478.2 | 465 | 581 | 637 | 594 | 551
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1658MW at 9:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1144 | 1234.49 | 1207.89 | 1178.29 | 1165.29 | 1143.79 | 1143.79 | 1216.49 | 1281.69 | 1429.99 | 1528.99 | 1340.19 | 1622.29 | 1658.49 | 1525.09 | 1584.79 | 1508.49 | 1463.29 | 1479.49 | 1509.59 | 1458.19 | 1255.69 | 1291.49 | 1590.39 | 1757.39 | 1614.19 | 1586.89 | 1616.09 | 1552.89 | 1568.89 | 1279.89 | 1209.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 25 | 28.5 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 86 | 28.5 | 25
Likhu-II(55) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7.8 | 7.8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 10 | 7.8
Super Dordi (54) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 54 | 11 | 11
Likhu-IV(52.4) | 13.2 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 52.4 | 16.3 | 0
Upper Marsyangdi "A"(50) | 29.7 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 50 | 29.7 | 28.8
Upper Bhotekoshi Khola(45) | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 45 | 16.9 | 16.9
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16
Mistri Khola(42) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 8 | 7.5
Upper Chameliya(40) | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 38.46 | 13.2 | 12.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13
Nyadi(30) | 8.8 | 7.8 | 7.8 | 7.8 | 7.5 | 7.5 | 7.5 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 30 | 8.8 | 7.3
Likhu Khola A(29.04) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 9 | 6.2
Lower Likhu(28) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 28 | 9 | 7.5
Dordi(27) | 7.3 | 7.4 | 7.4 | 7.4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 30 | 7.4 | 6
Upper Madi(25) | 8.4 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 25 | 8.4 | 8.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 25 | 7.5 | 7.5
Solu Khola(23.5) | 7.3 | 7.2 | 7.1 | 7.1 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 23.5 | 7.3 | 7.1
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 0 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 11.9 | 11.4 | 11.3 | 11.3 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 22 | 11.9 | 9.8
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 24.7 | 23.2 | 23.9 | 23.8 | 24.4 | 24.4 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 240 | 24.7 | 19.6
Total IPP | 483.95 | 487.95 | 487.65 | 487.65 | 484.65 | 484.65 | 484.65 | 481.85 | 481.85 | 481.85 | 481.85 | 478.15 | 478.15 | 461.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 474.75 | 1042.4 | 487.95 | 461.75
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 125 | 225 | 225 | 270 | 240 | 150 | 100 | 100 | 40 | 20 | 70 | 70 | 70 | 70 | 70 | 270 | 220 | 180 | 170 | 140 | 80 | 20 | 0 | 456 | 270 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 12.4 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 8 | 22.1 | 15.2 | 8
Total NEA SUBSIDIARIES | 39.4 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 65.2 | 160.2 | 260.2 | 260.2 | 305.2 | 275.2 | 185.3 | 135.3 | 135.3 | 75.3 | 55.3 | 105.3 | 105.3 | 105.3 | 105.3 | 105.3 | 305.3 | 255.3 | 222.2 | 212.2 | 182.2 | 122.2 | 62.2 | 35 | 538.1 | 305.3 | 35
KGA(144) | 30 | 0 | 0 | 0 | 0 | 0 | 60 | 97.9 | 102 | 102 | 121 | 121 | 71 | 62.3 | 62.3 | 126 | 123.8 | 99.2 | 95 | 88.5 | 0 | 32.9 | 61.6 | 89.1 | 101.4 | 61.3 | 55 | 44 | 30 | 0 | 0 | 144 | 126 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 35 | 35 | 35 | 45 | 45 | 35 | 25 | 25 | 70 | 35 | 25 | 35 | 35 | 0 | 25 | 50 | 60 | 60 | 45 | 35 | 35 | 25 | 0 | 0 | 70 | 70 | 0
MRS(69) | 36 | 0 | 0 | 0 | 0 | 0 | 40 | 46.1 | 46.1 | 46.1 | 57 | 57 | 47 | 34.2 | 34.2 | 46 | 33.2 | 46.5 | 46.4 | 46.4 | 35.1 | 35.1 | 35.1 | 66.4 | 68.7 | 50.2 | 36 | 32 | 16 | 16 | 16 | 69 | 68.7 | 0
U Trisuli 3A(60) | 40 | 40 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37.3 | 37.3 | 37.3 | 39.1 | 39.1 | 39.1 | 39.1 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 60 | 40 | 36.3
CHM(30) | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 15 | 23 | 27 | 10 | 10 | 0 | 0 | 0 | 10 | 10 | 10 | 15 | 10 | 10 | 10 | 10 | 30 | 27 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 4.5 | 3.7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8.3 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.8 | 11.5 | 11.3 | 11.3 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 14.1 | 11.6 | 9.8
MODI(14) | 5.3 | 3.2 | 3.2 | 3.4 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 14 | 5.3 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 160.14 | 83.74 | 81.54 | 81.74 | 81.84 | 81.84 | 214.84 | 270.84 | 274.94 | 274.94 | 314.14 | 314.14 | 234.14 | 202.74 | 202.74 | 338.24 | 296.24 | 284.44 | 269.34 | 262.04 | 114.74 | 171.44 | 225.14 | 303.94 | 318.54 | 246.44 | 220.94 | 200.94 | 160.94 | 105.94 | 105.94 | 489.91 | 338.24 | 81.54
KL1(60) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 60 | 0 | 0
KL2(32) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 32 | 0 | 0
KL3(14) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 69 | 77 | 61 | 65.4 | 66.6 | 66.6 | 65.8 | 65.4 | 65.4 | 65.4 | 56 | 54.2 | 62.3 | 61.8 | 56.9 | 61.4 | 67 | 64.8 | 68.2 | 61 | 53.1 | 69.6 | 52.9 | 66.3 | 45.4 | 67.4 | 67.2 | 62 | 60 | 73 | 55 |  | 77 | 45.4
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 412 | 420 | 400.9 | 380.3 | 386.5 | 386.5 | 411 | 393.4 | 375 | 375 | 160 | 151 | 291 | 296 | 394 | 414 | 431 | 471.4 | 463.1 | 442.9 | 408.7 | 384.7 | 381.1 | 241.2 | 192.9 | 247 | 256 | 250 | 340 | 385 | 408 |  | 471.4 | 151
RAMNAGAR |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6.2 | 6.5 | 6.1 | 5 | 5 | 50 | 52 | 53 | 48 | 48 | 26.6 | 10 | 14.8 | 14.8 | 23.8 | 80 | 80 | 100 | 100 | 57 |  | 100 | 5
RAXAUL 132 | 0: 0; 0.041667: 104; 0.083333: 107; 0.125: 110; 0.16667: 84; 0.20833: 84; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0; 0.375: 0; 0.41667: 0 |  | 110 | 0
NANPARA(33kV) | 0.8125: 4; 0.83333: 4; 0.85417: 4; 0.875: 4; 0.91667: 4; 0.95833: 4 |  | 4 | 4
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 |  | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 |  | Line 2
SAMPATIYA 132 kV | 70 | 0 | 0 | 0 | 0 | 0 | 0 |  | 68.6 | 68.6 | 66 | 63.4 | 61.2 | 61.4 | 66.1 | 79.8 | 69 | 76.8 | 75.9 | 64.2 | 51.1 | 59.1 | 61.2 | 71.1 | 72.5 | 71.3 | 71 | 69 | 77 | 75 | 70 |  | 79.8 | 0
Total IMPORT | 551 | 601 | 573.9 | 560.7 | 542.1 | 542.1 | 481.8 | 463.8 | 514 | 514 | 287 | 274.8 | 421 | 425.3 | 522 | 560.2 | 617 | 665 | 660.2 | 616.1 | 560.9 | 540 | 505.2 | 393.4 | 325.6 | 413.5 | 478.2 | 465 | 581 | 637 | 594 | 0 | 665 | 274.8
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1234.49 | 1207.89 | 1178.29 | 1165.29 | 1143.79 | 1143.79 | 1216.49 | 1281.69 | 1430.99 | 1530.99 | 1343.19 | 1372.29 | 1408.49 | 1275.09 | 1334.79 | 1508.49 | 1463.29 | 1479.49 | 1509.59 | 1458.19 | 1255.69 | 1291.49 | 1310.39 | 1477.39 | 1374.19 | 1356.89 | 1386.09 | 1322.89 | 1338.89 | 1279.89 | 1209.69 | 2231.81 | 1530.99 | 1143.79
Interruption/Tripping | 0: 0; 0.041667: 0; 0.083333: 0; 0.33333: 250; 0.375: 250; 0.41667: 250; 0.45833: 250; 0.75: 280; 0.77083: 280; 0.79167: 240; 0.8125: 230; 0.83333: 230; 0.85417: 230; 0.875: 230 |  | 280 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1234.49 | 1207.89 | 1178.29 | 1165.29 | 1143.79 | 1143.79 | 1216.49 | 1281.69 | 1430.99 | 1530.99 | 1343.19 | 1622.29 | 1658.49 | 1525.09 | 1584.79 | 1508.49 | 1463.29 | 1479.49 | 1509.59 | 1458.19 | 1255.69 | 1291.49 | 1590.39 | 1757.39 | 1614.19 | 1586.89 | 1616.09 | 1552.89 | 1568.89 | 1279.89 | 1209.69 | 1693.71 | 1757.39 | 1143.79
TOTAL NATIONAL LOAD (ACTUAL) | 1234.49 | 1207.89 | 1178.29 | 1165.29 | 1143.79 | 1143.79 | 1216.49 | 1281.69 | 1429.99 | 1528.99 | 1340.19 | 1622.29 | 1658.49 | 1525.09 | 1584.79 | 1508.49 | 1463.29 | 1479.49 | 1509.59 | 1458.19 | 1255.69 | 1291.49 | 1590.39 | 1757.39 | 1614.19 | 1586.89 | 1616.09 | 1552.89 | 1568.89 | 1279.89 | 1209.69 |  | 1757.39 | 1143.79
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0
NET IMPORT | 551 | 601 | 573.9 | 560.7 | 542.1 | 542.1 | 481.8 | 463.8 | 513 | 512 | 284 | 274.8 | 421 | 425.3 | 522 | 560.2 | 617 | 665 | 660.2 | 616.1 | 560.9 | 540 | 505.2 | 393.4 | 325.6 | 413.5 | 478.2 | 465 | 581 | 637 | 594 |  | 665 | 274.8
HZ | 49.95 | 49.99 | 49.99 | 49.97 | 50.02 | 50.02 | 49.95 | 49.99 | 49.89 | 49.89 | 49.98 | 50.023 | 50.089 | 49.951 | 49.939 | 49.965 | 50.176 | 49.98 | 49.88 | 50.04 | 50 | 50.1 | 49.97 | 50.02 | 49.96 | 49.961 | 50.058 | 50.058 | 49.98 | 50.012 | 50.01 |  | 50.176 | 49.88
HTD 132KV | 128 | 126.2 | 128.6 | 128.5 | 130.1 | 130.1 | 128.7 | 127.4 | 127.4 | 127.4 | 125 | 125.1 | 124.6 | 125.2 | 122.5 | 123.8 | 125.8 | 122.7 | 122.6 | 125.1 | 127 | 127 | 128.3 | 126.5 | 127.2 | 128.9 | 128.8 | 128.8 | 128.7 | 129.3 | 127.8 |  | 130.1 | 122.5
SUI 132KV | 131 | 130.1 | 131.9 | 132.1 | 133 | 133 | 132 | 130.4 | 130.4 | 130.4 | 126.8 | 126.4 | 126.3 | 126.8 | 125.4 | 126.3 | 128.2 | 126 | 126.1 | 127.9 | 129.3 | 129.3 | 130.6 | 126.9 | 128.6 | 129.5 | 128.9 | 128.9 | 131 | 132.3 | 132 |  | 133 | 125.4
DUBI 132KV | 129 | 129 | 129 | 128.8 | 130.2 | 130.2 | 127.3 | 127.5 | 127.5 | 127.5 | 128 | 126.3 | 126.9 | 128.3 | 123.2 | 125.3 | 127.3 | 125.8 | 126.8 | 129.4 | 129.2 | 129.2 | 129.1 | 127.3 | 130.7 | 130.7 | 129.9 | 129.9 | 131 | 131.1 | 128.3 |  | 131.1 | 123.2
ANAMANI 132KV | 131 | 129.9 | 129.5 | 131.7 | 131.7 | 131.7 | 130.6 | 130.2 | 130.2 | 130.2 | 127 | 125.5 | 127 | 129 | 124.9 | 127.3 | 129.9 | 128.5 | 128 | 130.2 | 130 | 130 | 129 | 129 | 131.4 | 133.2 | 131.7 | 131.7 | 133.5 | 133.7 | 132.3 |  | 133.7 | 124.9
KG-A 132KV | 134 | 133.5 | 132.9 | 131.6 | 133.3 | 133.3 | 134.3 | 133.7 | 133.7 | 133.7 | 133.5 | 133 | 132.9 | 132.9 | 131.4 | 132.7 | 135.2 | 132.9 | 131.8 | 134.6 | 135.5 | 135.5 | 136.7 | 132.6 | 133.6 | 135.5 | 135.6 | 135.6 | 136.2 | 136.3 | 134.7 |  | 136.7 | 131.4
KOHALPUR 132KV | 130 | 133.3 | 133 | 135.9 | 126.7 | 126.7 | 124 | 135 | 135 | 135 | 135 | 136.8 | 135.8 | 133.7 | 133.4 | 129.3 | 139.4 | 135.4 | 133.3 | 130.8 | 134.3 | 134.3 | 131.6 | 129.3 | 132.4 | 133.8 | 133 | 133 | 133.4 | 128.9 | 131.1 |  | 139.4 | 124
SUI 66KV | 66 | 66.6 | 66.5 | 66.6 | 67.1 | 67.1 | 66.2 | 65.4 | 65.4 | 65.4 | 63.7 | 63.4 | 63.3 | 63.5 | 62.8 | 63.6 | 64 | 63.3 | 63.4 | 64.3 | 65 | 65 | 65.8 | 64.2 | 65 | 65 | 65.1 | 65.1 | 65.8 | 66.6 | 66.1 |  | 67.1 | 62.8
[33 empty] | 0 | 0
Kathmandu Load | 184.54 | 140.3 | 133.1 | 129.24 | 138.54 | 171.84 | 194.22 | 244.74 | 245.74 | 246.74 | 362.14 | 347.04 | 320.94 | 347.264 | 42 | 345.14 | 304.14 | 314.72 | 312.24 | 183.24 | 313.16 | 325.74 | 358.32 | 410.38 | 414.02 | 387.455 | 345.94 | 345.94 | 277.44 | 220.74 | 149.44 |  | 414.02 | 42
MRS-SYU | 18 | -18.3 | -20 | -18.5 | -17.6 | -2.5 | 13.4 | 18.1 | 18.1 | 18.1 | 38 | 42.6 | 30 | 26.6 | 29.6 | 45.5 | 45.6 | 40.1 | 39.9 | 35.3 | 12.3 | 25.1 | 38.6 | 46.4 | 50.3 | 41.2 | 34.8 | 34.8 | 24.9 | 10.8 | 4.5 | 75 | 50.3 | -20
NMRS-MATA | 20 | -29.7 | -31.9 | -27.7 | -27.4 | -5.6 | 14.7 | 18.8 | 18.8 | 18.8 | 51 | 57.6 | 40.8 | 36.5 | 37.6 | 58.5 | 57.5 | 49.2 | 48.9 | 49.7 | 15.7 | 34.5 | 52.6 | 61.8 | 67 | 54.8 | 42.2 | 42.2 | 26.9 | 9 | 1.7 | 240 | 67 | -31.9
KL2-MATA | -31 | -13.2 | -14 | -15.3 | -12 | -14.6 | -16.3 | -2.9 | -2.9 | -2.9 | 33 | 28 | 32 | 33 | 15.9 | -4 | 0 | 0 | -3.3 | 2 | 31 | 30 | 37 | 41 | 54 | 48 | 42 | 42 | 26 | 11 | -29 | 240 | 54 | -31
KL1-SYU | -3 | -6.7 | -11 | -10.3 | -7.1 | -7 | -7.1 | -0.5 | 0.5 | 1.5 | 22 | 20.7 | 20 | 20.9 | 13.4 | 6.9 | 2.8 | 0 | 0 | 7.1 | 18.4 | 20.3 | 22.6 | 25.5 | 28 | 25.3 | 20 | 20 | 12.7 | 3 | -4.7 | 60 | 28 | -11
KHIMTI-LAMOSANGHU | 90 | 116.96 | 120.96 | 112 | 113.6 | 112.5 | 100.48 | 122.4 | 122.4 | 122.4 | 130 | 110 | 110 | 142.024 | 149.896 | 150 | 110 | 131.68 | 136.8 |  | 149.12 | 130.4 | 122.08 | 150.24 | 129.28 | 131.215 | 120 | 120 | 100 | 100 | 90 | 120 | 150.24 | 90
LAMOSHANGU-BHAKTAPUR | 72 | 83.7 | 86.8 | 81.4 | 83.1 | 83 | 74.9 | 87.2 | 87.2 | 87.2 | 87.2 | 91.5 | 97.5 | 93.5 | 96.2 | 88 | 85 | 89.2 | 91.8 | 83.74 | 97.6 | 88 | 83.3 | 97.7 | 86.7 | 88.6 | 91 | 91 | 90 | 81 | 75
BALAJU-SYUCHATAR | 41 | 77 | 78.5 | 70.4 | 71.7 | 58 | 45.8 | 29.5 | 29.5 | 29.5 | 29.5 | -27 | -7.6 | -3 | 7.9 | -2.8 | -4 | 6.5 | 12.2 | 3 | 18.6 | -5.3 | -29.3 | -36.9 | -57.9 | -42.7 | -19 | -19 | 9 | 32 | 64
DHALKE-NAWALPUR I | 84 | 91.5 | 85.9 | 82.5 | 81.2 | 83.5 | 88 | 89.8 | 89.8 | 89.8 | 89.8 | 78 | 89 | 83.8 | 96.3 | 101 | 95 | 96.1 | 103.8 | 94.9 | 92 | 81.1 | 72.5 | 77 | 56.2 | 65.1 | 65 | 65 | 76 | 68 | 85 |  | 103.8 | 56.2
N. BHARATPUR-BARDGHAT I | 9 | 29.4 | 29.9 | 25.6 | 28.1 | 25.1 | 22.5 | 11.4 | 11.4 | 11.4 | 11.4 | -11 | -3.6 | -4.6 | -4.3 | -10 | -26 | -16.4 | -15 | -9.2 | 6.3 | -4.7 | -7.5 | -10.5 | -13.5 | -9.9 | -5 | -5 | -3.6 | 2.8 | 5 |  | 29.9 | -26
DAMAK-DUHABI | -8 | -4.8 | -4.3 | -5 | -5.9 | -10.2 | -15 | -21.8 | -21.8 | -21.8 | -21.8 | -45 | -40 | -30.6 | -28.1 | -24 | -17 | -20 | -19.9 | -25.5 | -29.7 | -36.5 | -46.4 | -48.5 | -41.5 | -37.6 | -31 | -31 | -21 | -14 | -8 |  | -4.3 | -48.5
HETAUDA-KAMANE | 22 | 21.5 | 21.4 | 21.5 | 21.9 | 22.4 | 23.3 | 24.6 | 24.6 | 24.6 | 24.6 | 14 | 13.2 | 11.6 | 10.8 | 15 | 22 | 22.4 | 24.1 | 12.2 | 11.3 | 11.3 | 11.8 | 12.6 | 12.2 | 14.4 | 14 | 14 | 15 | 22 | 22 |  | 24.6 | 10.8
MIRCHAIYA LAHAN 2 | 91 | 81.1 | 81.4 | 83.1 | 80.8 | 85.8 | 90.4 | 91.8 | 91.8 | 91.8 | 91.8 | 87 | 83.5 | 91 | 117.7 | 110 | 103 | 109.6 | 114.9 | 113.2 | 96.7 | 95.4 | 104.8 | 116.6 | 107.1 | 99.9 | 103 | 103 | 100 | 97 | 95 |  | 117.7 | 80.8
Water Level
UTK |  | 1985.18 | 1985.35 | 1985.6 | 1985.78 | 1986.03 |  | 1986.12 |  | 1986.09 | 1985.8 | 1985.5 | 1985.28 | 1984.88 | 1984.8 | 1984.78 | 1984.62 | 1984.75 | 1984.88 | 1984.85 | 1984.85 |  | 1984.86 |  | 1984.51 |  | 1984.15 |  | 1983.9 | 1984 | 1984.2
KGA | 521.36 | 521.36 | 521.96 | 522.3 | 522.6 | 522.85 |  | 522.78 |  | 522.57 | 522.22 | 522.12 | 521.76 | 521.7 | 521.62 | 521.3 | 520.49 | 520.27 | 519.92 | 519.6 | 519.74 |  | 520 |  | 519.78 |  | 519.66 |  | 519.72 | 519.98 | 520.29
MMRS | 622.65 | 623.13 | 623.5 | 623.94 | 624.28 | 624.44 |  | 624.4 | 624.4 |  | 624.15 | 624.15 | 623.85 | 623.87 | 623.86 | 623.52 | 622.75 | 622.65 | 622.72 | 622.71 | 622.92 |  | 523.01 |  | 622.38 |  | 621.84 |  | 621.72 | 622.33 | 622.8
MRS | 335.27 | 335.5 | 336.03 | 336.48 | 336.91 | 337.17 |  |  | 337.11 | 336.92 | 336.57 | 336.53 | 336.15 | 335.88 | 335.68 | 335.36 | 335.25 | 335.34 | 335.31 | 335.2 | 335.21 |  | 335.55 |  | 335.45 |  | 335.2 |  | 335.12 | 335.26 | 335.4
CHM | 883.5 | 884 | 884.8 | 885.4 | 886 | 886.6 |  |  | 886.1 |  | 884.9 | 884.8 |  | 885.6 | 886.1 | 886.1 | 885.3 | 884.1 | 882.4 | 882.4 | 883.3 |  | 884 |  | 883.8 |  | 883.5 |  | 883.4 | 883.2 | 883.1
KL 1 | 0.27083: 1519.21
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1658.49; 0.041667: 9:00
9
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/9); 0.58333: Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/9)
IPP | bar: 0
NEA(RoR+PRoR) | 0.58333: Hrs.; 0.625: 0:00; 0.66667: 0.041667; 0.70833: 0.083333; 0.72917: 0.125; 0.75: 0.16667; 0.77083: 0.20833; 0.79167: 0.22917; 0.8125: 0.25; 0.83333: 0.27083; 0.85417: 0.29167; 0.875: 0.3125; 0.91667: 0.33333; 0.95833: 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
KL1+KL2+KL3 | 0.58333: T_Load; 0.625: 1234.49; 0.66667: 1207.89; 0.70833: 1178.29; 0.72917: 1165.29; 0.75: 1143.79; 0.77083: 1143.79; 0.79167: 1216.49; 0.8125: 1281.69; 0.83333: 1430.99; 0.85417: 1530.99; 0.875: 1343.19; 0.91667: 1622.29; 0.95833: 1658.49 | 1525.09 | 1584.79 | 1508.49 | 1463.29 | 1479.49 | 1509.59 | 1458.19 | 1255.69 | 1291.49 | 1590.39 | 1757.39 | 1614.19 | 1586.89 | 1616.09 | 1552.89 | 1568.89 | 1279.89 | 1209.69
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Water Level | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A2: Load Supply Group

## 10
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/10 |  |  | 2080/10/10 |  |  | Thursday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 520 | 545.6 | 568.3 | 553.4 | 613.2 | 582.5 | 578.7 | 610.9 | 469.5 | 317.1 | 265.2 | 423.8 | 449.4 | 498.6 | 672.9 | 698.1 | 678 | 735.3 | 720.8 | 522.2 | 502.4 | 482 | 489.7 | 372.3 | 357.9 | 461.7 | 542.5 | 652.3 | 601 | 533.2 | 535.5
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1668MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1110 | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1257.49 | 1346.69 | 1444.59 | 1476.19 | 1668.49 | 1661.89 | 1569.39 | 1499.09 | 1434.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1516.69 | 1615.79 | 1740.79 | 1750.49 | 1708.79 | 1533.79 | 1506.19 | 1432.39 | 1271.19 | 1182.19
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 27.8 | 27.8 | 27.8 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 27.8 | 27.8 | 27.5 | 27.5 | 27.5 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23.9 | 23.9 | 23.9 | 23.9 | 31.6 | 86 | 31.6 | 23.9
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 10
Super Dordi (54) | 11 | 11 | 11 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.2 | 10.2 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 54 | 11 | 10.1 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/10)
Likhu-IV(52.4) | 13 | 13 | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17.3 | 17.3 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 52.4 | 17.3 | 13
Upper Marsyangdi "A"(50) | 28.8 | 28.8 | 28.8 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.9 | 28.9 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 29.1 | 50 | 29.1 | 28.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 16.9 | 16.9 | 16.9 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14.3 | 14.3 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 45 | 16.9 | 14.3 |  | IPP | 474.75 | 474.75 | 474.75 | 474.95 | 474.95 | 474.95 | 474.95 | 474.95 | 476.05 | 472.25 | 472.25 | 472.25 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 468.65 | 468.65 | 468.65 | 476.35
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 95.1 | 255.1 | 410.5 | 214.3 | 164.2 | 74.2 | 74.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 116.5 | 350.5 | 190.4 | 80 | 40 | 37
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 8 | 7.5 |  | NEA ROR PROR | 89.94 | 79.94 | 79.94 | 80.44 | 97.44 | 97.44 | 197.94 | 276.64 | 310.14 | 259.04 | 213.24 | 209.24 | 263.74 | 282.54 | 264.24 | 255.74 | 252.84 | 167.04 | 216.54 | 276.94 | 263.04 | 181.44 | 161.54 | 135.64
Upper Chameliya(40) | 13.2 | 13.2 | 13.2 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 38.46 | 13.2 | 13 |  | IMPORT | 535.5 | 520 | 545.6 | 568.3 | 553.4 | 613.2 | 578.7 | 469.5 | 265.2 | 423.8 | 449.4 | 498.6 | 672.9 | 698.1 | 678 | 735.3 | 720.8 | 522.2 | 482 | 372.3 | 461.7 | 652.3 | 601 | 533.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 280 | 150 | 50 | 0 | 0
Nyadi(30) | 7.3 | 7.3 | 7.3 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 30 | 7.6 | 7.3 |  | System_Load | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1346.69 | 1476.19 | 1661.89 | 1569.39 | 1499.09 | 1434.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1615.79 | 1750.49 | 1533.79 | 1432.39 | 1271.19 | 1182.19
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 6.2 | 6.2 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.5 | 7.5 | 7.5 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 7.5 | 7.2 |  | National_Load | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1346.69 | 1476.19 | 1661.89 | 1569.39 | 1499.09 | 1434.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1615.79 | 1750.49 | 1533.79 | 1432.39 | 1271.19 | 1182.19
Dordi(27) | 6 | 6 | 6 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 30 | 6 | 5.8
Upper Madi(25) | 8.2 | 8.2 | 8.2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 10 | 8.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.5 | 7.5 | 7.5 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 25 | 7.5 | 7.4
Solu Khola(23.5) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 23.5 | 7.3 | 7.3
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 0 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.8 | 9.8 | 9.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 22 | 9.8 | 8.8
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 19.6 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 22.7 | 22.7 | 22.7 | 22.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.8 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18.9 | 20 | 21.1 | 24.7 | 25.6 | 240 | 25.6 | 18.9
Total IPP | 474.75 | 474.75 | 474.75 | 474.95 | 474.95 | 474.95 | 474.95 | 474.95 | 474.95 | 474.95 | 476.05 | 476.05 | 472.25 | 472.25 | 472.25 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 470.75 | 468.65 | 468.65 | 468.65 | 468.65 | 476.35 | 1042.4 | 476.35 | 468.65
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 60 | 60 | 220 | 325 | 370 | 180 | 130 | 40 | 40 | 15 | 15 | 15 | 15 | 15 | 15 | 76 | 150 | 310 | 300 | 150 | 100 | 40 | 0 | 0 | 456 | 370 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 32 | 32 | 29 | 60 | 32 | 26
Chilime(22.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 14.4 | 14.5 | 8.3 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 14.5 | 14.5 | 14.5 | 14.5 | 14.4 | 8 | 8 | 8 | 8 | 22.1 | 14.5 | 8
Total NEA SUBSIDIARIES | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 80.1 | 95.1 | 95.1 | 255.1 | 366.4 | 410.5 | 214.3 | 164.2 | 74.2 | 74.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 116.5 | 190.5 | 350.5 | 340.5 | 190.4 | 134 | 80 | 40 | 37 | 538.1 | 410.5 | 35.1
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3 | 60 | 66.1 | 90.2 | 90 | 60.7 | 61.2 | 61.2 | 71.1 | 80.9 | 71.5 | 71.5 | 91.6 | 33.5 | 30.9 | 45.4 | 60.9 | 72 | 70.1 | 71 | 60.9 | 40.8 | 30.7 | 30.7 | 144 | 91.6 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 50 | 60 | 60 | 60 | 50 | 22 | 22 | 43 | 45 | 45 | 35 | 35 | 24.8 | 24.6 | 24.9 | 46.4 | 46.4 | 45 | 45.2 | 44.2 | 24.5 | 24.9 | 0 | 70 | 60 | 0
MRS(69) | 0 | 0 | 0 | 0 | 17 | 17 | 17.5 | 39.7 | 56.7 | 55.4 | 62.3 | 62 | 49.8 | 35.4 | 35.4 | 40.5 | 44.2 | 35.5 | 45.2 | 45.2 | 31.9 | 32 | 52.6 | 50.9 | 50.9 | 50.9 | 51.2 | 35.3 | 35.5 | 23.3 | 22.3 | 69 | 62.3 | 0
U Trisuli 3A(60) | 37.8 | 37.8 | 37.8 | 38.3 | 38.3 | 38.3 | 38.3 | 39.8 | 39.8 | 38 | 37 | 35.3 | 35 | 36 | 36 | 37.8 | 37.1 | 36.3 | 34.3 | 34.3 | 34.5 | 34.5 | 36.3 | 36.3 | 36.3 | 36.3 | 38.3 | 38.3 | 38.3 | 40.3 | 40.3 | 60 | 40.3 | 34.3
CHM(30) | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 15 | 15 | 15 | 10 | 0 | 0 | 14 | 23 | 25 | 23 | 0 | 0 | 0 | 15 | 23 | 29 | 15 | 15 | 0 | 0 | 0 | 0 | 30 | 29 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 5.7 | 11.2 | 16.3 | 12.3 | 15 | 10 | 8.6 | 4.4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16.3 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 14.1 | 9.9 | 9.9
MODI(14) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 14 | 3.4 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 89.94 | 79.94 | 79.94 | 80.44 | 97.44 | 97.44 | 119.94 | 197.94 | 263.64 | 276.64 | 308.94 | 310.14 | 259.04 | 213.24 | 209.24 | 263.74 | 282.54 | 264.24 | 255.74 | 252.84 | 167.04 | 164.34 | 216.54 | 259.84 | 276.94 | 259.64 | 263.04 | 221.04 | 181.44 | 161.54 | 135.64 | 489.91 | 310.14 | 79.94
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 55 | 45 | 55 | 58.5 | 56.3 | 53.4 | 53.2 | 61.8 | 67.8 | 68.2 | 69.4 | 58.8 | 51.5 | 59.3 | 64.6 | 74.6 | 74.6 | 65.7 | 67.1 | 72.8 | 61.7 | 63.6 | 67.9 | 63.4 | 64.9 | 64.2 | 62.1 | 62.8 | 66.7 | 56 | 63.9 |  | 74.6 | 45
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 356 | 391 | 407 | 423 | 408.7 | 432 | 405.7 | 387 | 413 | 285.5 | 138.5 | 105 | 253.5 | 295.3 | 327 | 387 | 412 | 412 | 439.1 | 422.7 | 329.6 | 313.3 | 289.9 | 294.1 | 172.6 | 156 | 241 | 301 | 379 | 378 | 419 |  | 439.1 | 105
RAMNAGAR | 55 | 15 | 15 | 15 | 15 | 52 | 54 | 58 | 42.4 | 32 | 25.4 | 20 | 25 | 22 | 38 | 52 | 48 | 50.6 | 47 | 47 | 11.5 | 13.4 | 13.3 | 10.2 | 10.2 | 8.5 | 25 | 35 | 45.6 | 5 | 3 |  | 58 | 3
RAXAUL 132 | 20 | 24 | 22 | 23 | 23.4 | 22.8 | 22 | 23.8 | 25.6 | 25 | 26.4 | 26 | 30.2 | 0 | 0 | 91 | 102 | 83.6 | 106.2 | 105 | 60.4 | 59.7 | 51.2 | 53.2 | 53 | 57.4 | 60 | 70 | 92 | 91 | 0 |  | 106.2 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 49.5 | 45 | 46.6 | 48.8 | 50 | 53 | 47.6 | 48.1 | 62.1 | 58.8 | 57.4 | 55.4 | 63.6 | 72.8 | 69 | 68.3 | 61.5 | 66.1 | 75.9 | 73.3 | 59 | 52.4 | 59.7 | 68.8 | 71.6 | 71.8 | 73.6 | 73.7 | 69 | 71 | 47.3 |  | 75.9 | 45
Total IMPORT | 535.5 | 520 | 545.6 | 568.3 | 553.4 | 613.2 | 582.5 | 578.7 | 610.9 | 469.5 | 317.1 | 265.2 | 423.8 | 449.4 | 498.6 | 672.9 | 698.1 | 678 | 735.3 | 720.8 | 522.2 | 502.4 | 482 | 489.7 | 372.3 | 357.9 | 461.7 | 542.5 | 652.3 | 601 | 533.2 | 0 | 735.3 | 265.2
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1257.49 | 1346.69 | 1444.59 | 1476.19 | 1468.49 | 1461.89 | 1369.39 | 1299.09 | 1254.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1186.69 | 1285.79 | 1410.79 | 1470.49 | 1428.79 | 1383.79 | 1366.19 | 1382.39 | 1271.19 | 1182.19 | 2231.81 | 1510.99 | 1109.79
Interruption/Tripping | 0.3125: 200; 0.33333: 200; 0.375: 200; 0.41667: 200; 0.45833: 180; 0.72917: 330; 0.75: 330; 0.77083: 330; 0.79167: 280; 0.8125: 280; 0.83333: 150; 0.85417: 140; 0.875: 50 |  | 330 | 50
TOTAL SYSTEM LOAD (EXPECTED) | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1257.49 | 1346.69 | 1444.59 | 1476.19 | 1668.49 | 1661.89 | 1569.39 | 1499.09 | 1434.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1516.69 | 1615.79 | 1740.79 | 1750.49 | 1708.79 | 1533.79 | 1506.19 | 1432.39 | 1271.19 | 1182.19 | 1693.71 | 1750.49 | 1109.79
TOTAL NATIONAL LOAD (ACTUAL) | 1135.29 | 1109.79 | 1135.39 | 1158.79 | 1160.89 | 1220.69 | 1257.49 | 1346.69 | 1444.59 | 1476.19 | 1668.49 | 1661.89 | 1569.39 | 1499.09 | 1434.29 | 1481.59 | 1500.59 | 1462.19 | 1510.99 | 1493.59 | 1209.19 | 1516.69 | 1615.79 | 1740.79 | 1750.49 | 1708.79 | 1533.79 | 1506.19 | 1432.39 | 1271.19 | 1182.19 |  | 1750.49 | 1109.79
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
NET IMPORT | 535.5 | 520 | 545.6 | 568.3 | 553.4 | 613.2 | 582.5 | 578.7 | 610.9 | 469.5 | 317.1 | 265.2 | 423.8 | 449.4 | 498.6 | 672.9 | 698.1 | 678 | 735.3 | 720.8 | 522.2 | 502.4 | 482 | 489.7 | 372.3 | 357.9 | 461.7 | 542.5 | 652.3 | 601 | 533.2 |  | 735.3 | 265.2
HZ | 49.972 | 50.009 | 49.974 | 50.022 | 50 | 49.947 | 50.041 | 49.941 | 49.957 | 49.799 | 49.948 | 50.002 | 50.046 | 49.938 | 50.13 | 50.035 | 50.027 | 50.013 | 50.02 | 49.93 | 50.11 | 50.06 | 50.04 | 49.86 | 49.91 | 50 | 50.065 | 49.966 | 50.097 | 50.042 | 49.997 |  | 50.13 | 49.799
HTD 132KV | 130.6 | 127.9 | 127.2 | 127 | 127 | 127 | 125.9 | 125.3 | 124 | 128 | 126 | 125.1 | 126.6 | 125.3 | 127.8 | 125.5 | 123.9 | 123.9 | 122.7 | 124.9 | 124.9 | 130.9 | 129.9 | 128.7 | 127.4 | 128 | 129.1 | 127.9 | 128.8 | 128.2 | 126.7 |  | 130.9 | 122.7
SUI 132KV | 134.4 | 132.1 | 131.6 | 131 | 131 | 131 | 130 | 129.4 | 129.4 | 129.6 | 127 | 127.1 | 128.6 | 127.5 | 129.5 | 127.9 | 126.9 | 126.7 | 125.9 | 127.1 | 127.1 | 132.2 | 131.4 | 129.9 | 128.3 | 128.8 | 129.9 | 129.2 | 130.7 | 130.7 | 130.3 |  | 134.4 | 125.9
DUBI 132KV | 130.5 | 131 | 128.7 | 1274.5 | 1274.5 | 1274.5 | 129.8 | 128 | 128 | 127 | 125.4 | 125.6 | 130.8 | 129.3 | 127.7 | 128.3 | 127.6 | 127.2 | 128.9 | 128 | 128 | 132.8 | 131.1 | 126.1 | 128.9 | 130.8 | 131.7 | 130.9 | 129.8 | 129.4 | 130.4 |  | 1274.5 | 125.4
ANAMANI 132KV | 132.6 | 132.9 | 130.6 | 130 | 130 | 130 | 130 | 130 | 130 | 128.8 | 125.6 | 126 | 130.8 | 130 | 129.4 | 130.2 | 129.9 | 129.6 | 130.2 | 129.3 | 129.3 | 133.7 | 131.5 | 127 | 130.1 | 132.2 | 132.4 | 133.2 | 132.3 | 133.2 | 134 |  | 134 | 125.6
KG-A 132KV | 137.9 | 132.7 | 131.1 | 131 | 131 | 131 | 135 | 134.6 | 134.6 | 135.4 | 132.6 | 132.1 | 132.5 | 131.5 | 131.8 | 131.2 | 130 | 130.1 | 132.6 | 134.6 | 134.6 | 136 | 135.9 | 133.5 | 133.2 | 133.9 | 134.5 | 134.2 | 135.2 | 131.4 | 130.3 |  | 137.9 | 130
KOHALPUR 132KV | 133.9 | 131.8 | 130.6 | 134.7 | 134.7 | 134.7 | 135 | 126 | 126 | 129.9 | 130.4 | 131.5 | 131.8 | 130.1 | 127.5 | 131 | 127 | 130.7 | 132.1 | 129.6 | 129.6 | 132.9 | 132.2 | 130 | 133.3 | 132.5 | 132.4 | 132.8 | 133.8 | 133.4 | 128.5 |  | 135 | 126
SUI 66KV | 67.3 | 66.5 | 66.4 | 66.2 | 66.2 | 66 | 65.3 | 65.1 | 64.2 | 64.8 | 63.9 | 63.8 | 64.8 | 64.2 | 65.3 | 64.3 | 63.8 | 63.7 | 63.4 | 63.7 | 63.7 | 66.6 | 65.9 | 65.1 | 64.5 | 64.8 | 64.9 | 64.9 | 65.8 | 65.7 | 65.6 |  | 67.3 | 63.4
[33 empty] | 0 | 0
Kathmandu Load | 135.04 | 117.94 | 113.64 | 125.64 | 133.74 | 165.04 | 200.44 | 247.54 | 297.84 | 321.64 | 383.54 | 376.593 | 349.722 | 354.601 | 42 | 326.653 | 337.554 | 333.558 | 344.02 | 352.66 | 283.64 | 259.76 | 276.9 | 319.48 | 366 | 365.62 | 361.172 | 342.189 | 275.174 | 235.184 | 173.46 |  | 383.54 | 42
MRS-SYU | 3.1 | -6 | -8.6 | -14.2 | -8.9 | -3.1 | 3.2 | 17.7 | 30.7 | 26.7 | 35.7 | 38.9 | 33.8 | 28.9 | 34.7 | 31.9 | 39.8 | 35 | 34.7 | 41.8 | 24.1 | 20.7 | 25.1 | 30.2 | 30.6 | 30.5 | 34.1 | 29.2 | 13.5 | 7.6 | -5.6 | 75 | 41.8 | -14.2
NMRS-MATA | 0 | -12 | -15 | -23 | -17.2 | -10.7 | -1.7 | 20 | 35.8 | 39.2 | 48.3 | 53 | 47.5 | 40 | 44.8 | 38.3 | 49.6 | 43.2 | 40.8 | 48.5 | 33.4 | 29.2 | 34.8 | 41.8 | 41.4 | 40.7 | 46.4 | 40.7 | 12.2 | 5.3 | -11.7 | 240 | 53 | -23
KL2-MATA | -30 | -26 | -32 | -30.1 | -27.6 | -24.1 | -18.2 | -17 | -11.4 | 17.1 | 34.7 | 29.3 | 27.2 | 30.2 | 34 | 20 | 19.2 | 23 | 27 | 21 | 30 | 19 | 17 | 27 | 39 | 39 | 37 | 31 | 18 | 7.3 | -23 | 240 | 39 | -32
KL1-SYU | -5 | -5 | -7.7 | -9.7 | -10.2 | -9.7 | -5.5 | -2.3 | 3.6 | 19.3 | 23.1 | 21.5 | 21 | 23 | 21.9 | 10.8 | 8.5 | 9.9 | 8.9 | 12.1 | 23.4 | 22.6 | 22.1 | 22.1 | 25.9 | 26 | 23 | 12.1 | 9.8 | 3 | -2.9 | 60 | 26 | -10.2
KHIMTI-LAMOSANGHU | 80 | 80 | 90 | 115 | 110 | 125 | 135 | 140 | 150 | 132 | 153 | 143.453 | 124.582 | 130.761 | 100.868 | 123.413 | 123.914 | 128.118 | 144.48 | 141.12 | 88.8 | 84.32 | 92.16 | 112.64 | 143.36 | 143.68 | 132.932 | 141.449 | 133.934 | 122.244 | 126.92 | 120 | 153 | 80
LAMOSHANGU-BHAKTAPUR | 69 | 75 | 78 | 85.8 | 81.2 | 87.3 | 90.3 | 88.8 | 90.3 | 82.9 | 97.5 | 92.9 | 83.4 | 87.6 | 70.3 | 82.8 | 82.5 | 85.9 | 94.6 | 94 | 70.6 | 64.6 | 68.6 | 77.7 | 95 | 94 | 87.3 | 92.1 | 89.1 | 84.1 | 87.1
BALAJU-SYUCHATAR | 63 | 71 | 71 | 80 | 73.7 | 65.2 | 62.3 | 41.7 | 13.3 | -26.5 | -12.6 | -17 | -10.6 | 3.3 | -15.3 | 13.3 | 80.8 | 10.1 | 14.1 | -4.6 | 2.2 | 16.3 | 8.8 | -9.6 | -26.5 | -21.7 | -31.5 | -14.1 | -31.6 | 38.3 | 75
DHALKE-NAWALPUR I | 77 | 83 | 94 | 104.96 | 91.8 | 102.9 | 98.5 | 97.4 | 98.2 | 76.4 | 75.1 | 70.7 | 66.8 | 77.7 | 52.1 | 71.5 | 72.5 | 80.1 | 83.6 | 82.6 | 57.3 | 54.2 | 52.2 | 57.8 | 68.4 | 65 | 66 | 71.2 | 77 | 77.6 | 100.2 |  | 104.96 | 52.1
N. BHARATPUR-BARDGHAT I | 6 | 20 | 23 | 29.3 | 28.8 | 17.7 | 13.4 | 6.8 | -2.9 | 1.9 | -5.3 | -6.5 | -3.6 | -9.3 | -6.5 | -3.8 | -8.9 | -4 | -5.6 | -4.3 | -1.8 | 0 | -4.2 | -4.9 | -4 | -2.1 | -3.6 | -1.5 | 16.4 | 19.5 | 23.2 |  | 29.3 | -9.3
DAMAK-DUHABI | -6 | -4 | -3.4 | -2.8 | -3.8 | -6.5 | -11.8 | -16.6 | -27.2 | -36.8 | -42.5 | -40.4 | -36.5 | -28.1 | -25 | 20.4 | -17.1 | -16.4 | -19.7 | -20.7 | -29.3 | -31.8 | -43.4 | -46.1 | -42.9 | -39.2 | -34.8 | -27.3 | -14.5 | -10.7 | -6.2 |  | 20.4 | -46.1
HETAUDA-KAMANE | 21 | 21 | 21.8 | 22.1 | 21.7 | 23.1 | 23.5 | 24.74 | 25.8 | 12.7 | 12 | 12.3 | 13 | 12.1 | 13 | 16 | 25.3 | 21.7 | 25.2 | 24.4 | 6 | 5.4 | 8.7 | 8.8 | 7.2 | 8.9 | 8.7 | 8.8 | 16.2 | 16.3 | 20.9 |  | 25.8 | 5.4
MIRCHAIYA LAHAN 2 | 80 | 82 | 83 | 79.3 | 81.1 | 82.3 | 84 | 89.8 | 94 | 94 | 104.3 | 106 | 94.7 | 86.5 | 88.1 | 102.1 | 102.7 | 96.3 | 106.78 | 104.6 | 92.7 | 91.8 | 102 | 113.1 | 108.6 | 106.9 | 102.7 | 97.2 | 97.3 | 94.3 | 88.6 |  | 113.1 | 79.3
Water Level
UTK | 1984.43 | 1984.68 | 1984.9 | 1985.11 | 1985.33 | 1985.52 |  | 1985.62 |  | 1985.59 |  | 1985.05 | 1984.2 | 1983.95 | 1983.96 | 1984.05 | 1984.2 | 1984.35 | 1984.48 | 1984.52 | 1984.55 |  | 1984.75 |  | 1984.4 |  | 1983.8 |  | 1983.65 | 1983.84 | 1984.1
KGA | 520.6 | 521.03 | 521.37 | 521.72 | 522.03 | 522.33 |  | 522.63 |  | 522.49 |  | 522.46 | 522.35 | 522.31 | 522.25 | 522.16 | 522.1 | 521.94 | 521.86 | 521.72 | 521.5 |  | 521.55 |  | 521.51 |  | 521.41 |  | 521.35 | 521.45 | 521.59
MMRS | 623.26 | 623.65 | 624 | 624.44 | 624.66 | 625.04 |  | 625.16 |  | 624.91 |  | 624.4 | 624.1 | 624.17 | 624.24 | 624.06 | 623.75 | 623.55 | 623.24 | 623.2 | 623.21 |  | 623.21 |  | 623 |  | 622.55 |  | 622.39 | 622.39 | 622.8
MRS | 335.72 | 336.15 | 336.47 | 336.8 | 336.94 | 336.99 |  | 336.98 |  | 336.68 |  | 336.33 | 335.93 | 335.61 | 335.4 | 335.11 | 335.17 | 335.33 | 335.44 | 335.36 | 335.19 |  | 335.28 |  | 335.31 |  | 335.31 |  | 335.33 | 335.35 | 335.52
CHM | 883.1 | 883.5 | 884.3 | 885.1 | 885.5 | 886 |  | 886.5 |  | 886.3 |  | 885.9 | 885.7 | 885.9 | 886.4 | 886.4 | 885.8 | 884.5 | 883.1 | 883.5 | 884.3 |  | 884.8 |  | 883.8 |  | 882.6 |  | 882.8 | 883.7 | 884.4
KL 1 | 0: 1519.24; 0.20833: 1519.24; 0.25: 1519.25; 0.33333: 1519.25; 0.54167: 1519.26; 0.83333: 1519.28
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1668.49; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/10)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 11
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/11 |  |  | 2080/10/11 |  |  | Friday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 525.9 | 515 | 536.1 | 550.6 | 581 | 539.9 | 556.2 | 603.7 | 523.3 | 326.4 | 217.8 | 369.8 | 520.4 | 591.9 | 667.7 | 666.8 | 667 | 709 | 663.5 | 662.5 | 509 | 508.4 | 448 | 253.3 | 352.2 | 425.6 | 486.9 | 480.4 | 536.7 | 534 | 518.4
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1677MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1133 | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1275.49 | 1339.59 | 1458.889 | 1507.49 | 1677.29 | 1595.19 | 1471.39 | 1378.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1457.89 | 1383.09 | 1377.09 | 1393.59 | 1554.69 | 1767.45 | 1745.45 | 1718.19 | 1605.09 | 1562.29 | 1454.99 | 1378.59 | 1278.19
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 31.6 | 31.6 | 31.6 | 31.8 | 31.8 | 31.8 | 27.2 | 27.2 | 29.5 | 26.6 | 26.6 | 29.5 | 28.8 | 21 | 26 | 25.39 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.9 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 86 | 31.8 | 21
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 | [26 empty] | 11
Super Dordi (54) | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 0 | 18 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 54 | 18 | 0 | [26 empty] | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/11)
Likhu-IV(52.4) | 13.2 | 13.2 | 13.2 | 17.7 | 17.7 | 17.7 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 52.4 | 17.7 | 13.2
Upper Marsyangdi "A"(50) | 29.1 | 29.1 | 29.1 | 28.6 | 28.6 | 28.6 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 50 | 29.1 | 28.3 | [26 empty] | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 45 | 15.1 | 14.8 | [26 empty] | IPP | 476.35 | 467.55 | 478.55 | 482.75 | 482.75 | 482.75 | 477.75 | 477.15 | 480.05 | 479.35 | 454.45 | 476.45 | 477.04 | 481.15 | 481.15 | 481.15 | 481.15 | 481.15 | 481.55 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 | [26 empty] | NEA SUB | 36 | 37.1 | 36 | 36 | 36 | 36 | 51 | 186 | 291.1 | 125.2 | 65.3 | 70.3 | 50.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 75.2 | 382.2 | 192.2 | 152.2 | 92.2 | 72.2
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7.5 | [26 empty] | NEA ROR PROR | 151.34 | 134.74 | 124.24 | 78.14 | 78.14 | 140.14 | 254.64 | 321.04 | 326.24 | 267.04 | 238.04 | 266.64 | 251.34 | 252.54 | 247.54 | 233.54 | 205.24 | 201.24 | 214.54 | 352.6 | 259.94 | 245.04 | 272.34 | 194.64
Upper Chameliya(40) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 38.46 | 13 | 13 | [26 empty] | IMPORT | 518.4 | 525.9 | 515 | 536.1 | 550.6 | 581 | 556.2 | 523.3 | 217.8 | 369.8 | 520.4 | 591.9 | 667.7 | 666.8 | 667 | 709 | 663.5 | 662.5 | 508.4 | 253.3 | 425.6 | 480.4 | 536.7 | 534
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 | [26 empty] | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 | [26 empty] | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 230 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 250 | 100 | 0 | 0
Nyadi(30) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 30 | 7.6 | 7.6 | [26 empty] | System_Load | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1339.59 | 1507.49 | 1595.19 | 1471.39 | 1378.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1458.89 | 1385.09 | 1380.09 | 1559.69 | 1745.45 | 1605.09 | 1454.99 | 1378.59 | 1278.19
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 6.2 | 6.2 | [26 empty] | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -2 | -3 | -5 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 7.2 | 7.2 | [26 empty] | National_Load | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1339.59 | 1507.49 | 1595.19 | 1471.39 | 1378.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1457.89 | 1383.09 | 1377.09 | 1554.69 | 1745.45 | 1605.09 | 1454.99 | 1378.59 | 1278.19
Dordi(27) | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 30 | 6.3 | 5.8
Upper Madi(25) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 10 | 10
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 0 | 0 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 25 | 8.2 | 0
Solu Khola(23.5) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 23.5 | 7.3 | 7.3
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 0 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 8.8 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 11 | 0
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 25.6 | 26 | 28 | 28 | 28 | 28 | 28.1 | 25.8 | 24.7 | 22.1 | 22.1 | 22.8 | 22.9 | 24.1 | 17.6 | 19 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.6 | [7 empty] | 240 | 28.1 | 17.1
Total IPP | 476.35 | 467.55 | 478.55 | 482.75 | 482.75 | 482.75 | 477.75 | 477.75 | 480.05 | 477.15 | 477.15 | 480.05 | 479.35 | 454.45 | 476.45 | 477.04 | 481.15 | 481.15 | 481.15 | 481.15 | 481.15 | 481.15 | 481.55 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 1042.4 | 482.75 | 454.45
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 45 | 150 | 260 | 250 | 90 | 30 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 340 | 240 | 150 | 90 | 110 | 50 | 30 | 456 | 340 | 0
Khimti Khola(60) | 28 | 28 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 28 | 27
Chilime(22.1) | 8 | 9.1 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 14.2 | 14.1 | 8.2 | 8.3 | 8.3 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 15.1 | 15.2 | 15.1 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 22.1 | 15.2 | 8
Total NEA SUBSIDIARIES | 36 | 37.1 | 36 | 36 | 36 | 36 | 36 | 51 | 81 | 186 | 301.2 | 291.1 | 125.2 | 65.3 | 70.3 | 50.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 75.2 | 222.1 | 382.2 | 282.1 | 192.2 | 132.2 | 152.2 | 92.2 | 72.2 | 538.1 | 382.2 | 35.2
KGA(144) | 48.7 | 30.5 | 30.3 | 0 | 0 | 0 | 60 | 61.1 | 90 | 111.6 | 111 | 91 | 81.6 | 60.9 | 86.1 | 61 | 60 | 60 | 60 | 60 | 60 | 30 | 62.8 | 140 | 142.8 | 136.2 | 91.2 | 91.2 | 70.4 | 91.4 | 45 | 144 | 142.8 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 30 | 45.2 | 70 | 70 | 70 | 70 | 70 | 36.5 | 36.3 | 36.2 | 36 | 35.3 | 35.3 | 35.3 | 22 | 22 | 0 | 24.4 | 34.8 | 34.8 | 34.8 | 29.8 | 35.4 | 35.4 | 35.4 | 35.4 | 70 | 70 | 0
MRS(69) | 22 | 22.1 | 15.8 | 0 | 0 | 22 | 15.6 | 15.5 | 32.3 | 36.9 | 36.9 | 51.5 | 51.2 | 46.9 | 46.6 | 46 | 47 | 47 | 41 | 33 | 33 | 17 | 42.1 | 68 | 68.8 | 68.3 | 51.9 | 52.2 | 52.2 | 55.3 | 34 | 69 | 68.8 | 0
U Trisuli 3A(60) | 36.8 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.2 | 38.2 | 38.999 | 39.1 | 39 | 38.8 | 36.8 | 38.8 | 39.8 | 39.8 | 37.3 | 35 | 35 | 35 | 35 | 35 | 35 | 35.3 | 37.3 | 37.3 | 37.1 | 37.1 | 37.1 | 40.3 | 40.3 | 60 | 40.3 | 35
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 30 | 23 | 23 | 23 | 28 | 10 | 0 | 0 | 10 | 15 | 15 | 10 | 10 | 10 | 0 | 10 | 22 | 27 | 10 | 10 | 10 | 10 | 10 | 0 | 30 | 30 | 0 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 2.8 | 7.1 | 11.1 | 15.3 | 18.1 | 18.7 | 18.1 | 15 | 12 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.7 | 0 |  | Tanakpur | 61 | 59.4 | 57.1 | 57.6 | 58 | 63.2 | 58.8 | 48 | 53.4 | 58.9 | 70 | 64 | 65.6 | 72 | 68 | 67 | 66 | 63.6 | 56.2 | 58.1 | 67.4 | 62.7 | 69 | 62.2
TRI(24) | 15 | 15 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 24 | 15 | 11 |  | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4 |  | Muz | 398 | 391.6 | 376 | 384 | 420 | 395 | 345 | 74 | 218 | 363.5 | 399.9 | 402 | 395 | 398 | 427 | 440 | 440 | 379 | 108 | 262.8 | 329 | 396 | 365 | 395.2
DEVI(14.1) | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 14.1 | 11.6 | 8.7 |  | Ram | 12 | 13 | 5 | 5 | 5 | 6 | 7 | 5 | 5 | 2 | 20 | 50 | 48 | 58 | 66 | 20 | 20 | 5 | 27 | 28 | 33 | 3 | 3 | 12
MODI(14) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 14 | 3.2 | 3.2 |  | Rax | 0 | 0 | 98 | 104 | 98 | 92 | 68 | 30.8 | 30 | 26 | 27 | 80 | 89 | 94 | 104 | 94 | 94 | 26.8 | 27 | 36.4 | 0 | 25 | 26 | 0
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 |  | Sam | 55 | 51 | 0 | 0 | 0 | 0 | 44.5 | 60 | 63.4 | 70 | 75 | 71.7 | 69.2 | 45 | 44 | 42.5 | 42.5 | 34 | 35.1 | 40.3 | 51 | 50 | 71 | 49
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 |  |  | 61 | 59.4 | 57.1 | 57.6 | 58 | 63.2 | 58.8 | 48 | 53.4 | 58.9 | 70 | 64 | 65.6 | 72 | 68 | 67 | 66 | 63.6 | 56.2 | 58.1 | 67.4 | 62.7 | 69 | 62.2
Total ROR | 151.34 | 134.74 | 124.24 | 78.14 | 78.14 | 140.14 | 221.84 | 254.64 | 294.139 | 321.04 | 322.54 | 326.24 | 267.04 | 238.04 | 266.64 | 251.34 | 252.54 | 247.54 | 233.54 | 205.24 | 201.24 | 122.24 | 214.54 | 340 | 352.6 | 326.54 | 259.94 | 265.84 | 245.04 | 272.34 | 194.64 | 489.91 | 352.6 | 78.14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 |  |  | 398 | 391.6 | 376 | 384 | 420 | 395 | 345 | 74 | 218 | 363.5 | 399.9 | 402 | 395 | 398 | 427 | 440 | 440 | 379 | 108 | 262.8 | 329 | 396 | 365 | 395.2
KL2(32) | [31 empty] | 32 | 0 | 0 |  |  | 12 | 13 | 5 | 5 | 5 | 6 | 7 | 5 | 5 | 2 | 20 | 50 | 48 | 58 | 66 | 20 | 20 | 5 | 27 | 28 | 33 | 3 | 3 | 12
KL3(14) | [31 empty] | 14 | 0 | 0 |  |  | 0 | 0 | 98 | 104 | 98 | 92 | 68 | 30.8 | 30 | 26 | 27 | 80 | 89 | 94 | 104 | 94 | 94 | 26.8 | 27 | 36.4 | 0 | 25 | 26 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 |  |  | 55 | 51 | 0 | 0 | 0 | 0 | 44.5 | 60 | 63.4 | 70 | 75 | 71.7 | 69.2 | 45 | 44 | 42.5 | 42.5 | 34 | 35.1 | 40.3 | 51 | 50 | 71 | 49
TANAKPUR | 62.2 | 61.1 | 59.4 | 57.1 | 57.6 | 58 | 62.9 | 63.2 | 55.3 | 58.8 | 62.5 | 48 | 53.4 | 58.9 | 70 | 64 | 65.6 | 72 | 68 | 67 | 66 | 65 | 63.6 | 68 | 56.2 | 43.6 | 58.1 | 60.1 | 67.4 | 62.7 | 69 |  | 72 | 43.6
KATAIYA | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0 |  | 0 | 0
MUJAFFARPUR | 395.2 | 397.5 | 391.6 | 376 | 384 | 420 | 371 | 395 | 399 | 345 | 128 | 74 | 218 | 363.5 | 399.9 | 402 | 395 | 398 | 427 | 440 | 440 | 378 | 379 | 316 | 108 | 220 | 262.8 | 306 | 329 | 396 | 365 |  | 440 | 74
RAMNAGAR | 12 | 12 | 13 | 5 | 5 | 5 | 5 | 6 | 6 | 7 | 6 | 5 | 5 | 2 | 20 | 50 | 48 | 58 | 66 | 20 | 20 | 10 | 5 | 4 | 27 | 26 | 28 | 28 | 33 | 3 | 3 |  | 66 | 2 | [9 empty] | 61 | 0 | 398 | 12 | 0 | 55
RAXAUL 132 | 0 | 0 | 0 | 98 | 104 | 98 | 101 | 92 | 106 | 68 | 56.2 | 30.8 | 30 | 26 | 27 | 80 | 89 | 94 | 104 | 94 | 94 | 24 | 26.8 | 28 | 27 | 28.2 | 36.4 | 50 | 0 | 25 | 26 |  | 106 | 0 | [9 empty] | 59.4 | 0 | 391.6 | 13 | 0 | 51
NANPARA(33kV) | 0: 0; 0.041667: 0; 0.083333: 0 |  | 0 | 0 | [9 empty] | 57.1 | 0 | 376 | 5 | 98 | 0
BISHANPUR(33kV) | 0: 0; 0.041667: 0; 0.083333: 0 |  | 0 | 0 | [9 empty] | 57.6 | 0 | 384 | 5 | 104 | 0 | [11 empty] | UTK Discharge Test
JALESHWOR(33kV) | 0: 0; 0.041667: 0; 0.083333: 0 |  | 0 | 0 | [9 empty] | 58 | 0 | 420 | 5 | 98 | 0
RAJBIRAJ(33kV) | 0: 0; 0.041667: 0; 0.083333: 0 |  | 0 | 0 | Line1 | [8 empty] | 63.2 | 0 | 395 | 6 | 92 | 0
RAXAUL(33kV) | 0: 0; 0.041667: 0; 0.083333: 0 |  | 0 | 0 | Line 2 | [8 empty] | 58.8 | 0 | 345 | 7 | 68 | 44.5
SAMPATIYA 132 kV | 49 | 55.3 | 51 | 0 | 0 | 0 |  | 0 | 37.4 | 44.5 | 73.7 | 60 | 63.4 | 70 | 75 | 71.7 | 69.2 | 45 | 44 | 42.5 | 42.5 | 32 | 34 | 32 | 35.1 | 34.4 | 40.3 | 42.8 | 51 | 50 | 71 |  | 75 | 0 | [9 empty] | 48 | 0 | 74 | 5 | 30.8 | 60
Total IMPORT | 518.4 | 525.9 | 515 | 536.1 | 550.6 | 581 | 539.9 | 556.2 | 603.7 | 523.3 | 326.4 | 217.8 | 369.8 | 520.4 | 591.9 | 667.7 | 666.8 | 667 | 709 | 663.5 | 662.5 | 509 | 508.4 | 448 | 253.3 | 352.2 | 425.6 | 486.9 | 480.4 | 536.7 | 534 | 0 | 709 | 217.8 | [9 empty] | 53.4 | 0 | 218 | 5 | 30 | 63.4
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [9 empty] | 58.9 | 0 | 363.5 | 2 | 26 | 70
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [9 empty] | 70 | 0 | 399.9 | 20 | 27 | 75
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [9 empty] | 64 | 0 | 402 | 50 | 80 | 71.7
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [9 empty] | 65.6 | 0 | 395 | 48 | 89 | 69.2
TOTAL SYSTEM LOAD (ACTUAL) | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1275.49 | 1339.59 | 1458.889 | 1507.49 | 1427.29 | 1315.19 | 1241.39 | 1278.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1458.89 | 1385.09 | 1380.09 | 1147.59 | 1279.69 | 1487.45 | 1465.45 | 1438.19 | 1355.09 | 1362.29 | 1354.99 | 1378.59 | 1278.19 | 2231.81 | 1507.49 | 1132.99 | [9 empty] | 72 | 0 | 398 | 58 | 94 | 45
Interruption/Tripping | 0.3125: 250; 0.33333: 280; 0.375: 230; 0.41667: 100; 0.72917: 250; 0.75: 280; 0.77083: 280; 0.79167: 280; 0.8125: 280; 0.83333: 250; 0.85417: 200; 0.875: 100 |  | 280 | 100 | [9 empty] | 68 | 0 | 427 | 66 | 104 | 44
TOTAL SYSTEM LOAD (EXPECTED) | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1275.49 | 1339.59 | 1458.889 | 1507.49 | 1677.29 | 1595.19 | 1471.39 | 1378.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1458.89 | 1385.09 | 1380.09 | 1397.59 | 1559.69 | 1767.45 | 1745.45 | 1718.19 | 1605.09 | 1562.29 | 1454.99 | 1378.59 | 1278.19 | 1693.71 | 1767.45 | 1132.99 | [9 empty] | 67 | 0 | 440 | 20 | 94 | 42.5
TOTAL NATIONAL LOAD (ACTUAL) | 1182.09 | 1165.29 | 1153.79 | 1132.99 | 1147.49 | 1239.89 | 1275.49 | 1339.59 | 1458.889 | 1507.49 | 1677.29 | 1595.19 | 1471.39 | 1378.19 | 1405.29 | 1446.28 | 1435.69 | 1430.89 | 1457.89 | 1383.09 | 1377.09 | 1393.59 | 1554.69 | 1767.45 | 1745.45 | 1718.19 | 1605.09 | 1562.29 | 1454.99 | 1378.59 | 1278.19 |  | 1767.45 | 1132.99 | [9 empty] | 66 | 0 | 440 | 20 | 94 | 42.5
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [9 empty] | 63.6 | 0 | 379 | 5 | 26.8 | 34
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [9 empty] | 56.2 | 0 | 108 | 27 | 27 | 35.1
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [9 empty] | 58.1 | 0 | 262.8 | 28 | 36.4 | 40.3
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [9 empty] | 67.4 | 0 | 329 | 33 | 0 | 51
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [9 empty] | 62.7 | 0 | 396 | 3 | 25 | 50
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | [9 empty] | 69 | 0 | 365 | 3 | 26 | 71
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | [9 empty] | 62.2 | 0 | 395.2 | 12 | 0 | 49
NET IMPORT | 518.4 | 525.9 | 515 | 536.1 | 550.6 | 581 | 539.9 | 556.2 | 603.7 | 523.3 | 326.4 | 217.8 | 369.8 | 520.4 | 591.9 | 667.7 | 666.8 | 667 | 708 | 661.5 | 659.5 | 505 | 503.4 | 448 | 253.3 | 352.2 | 425.6 | 486.9 | 480.4 | 536.7 | 534 |  | 708 | 217.8
HZ | 50.027 | 50.002 | 50.059 | 50.003 | 49.974 | 49.946 | 50.03 | 49.931 | 50.03 | 50.004 | 49.912 | 50.056 | 50.122 | 50.002 | 50.007 | 49.901 | 49.913 | 50.04 | 50.04 | 49.9 | 49.9 | 49.91 | 50.073 | 50.03 | 49.872 | 49.899 | 50.078 | 50.004 | 50.05 | 50.03 | 50.006 |  | 50.122 | 49.872
HTD 132KV | 127.7 | 127.9 | 128.2 | 129 | 128 | 127 | 129.1 | 127.5 | 126.9 | 128.2 | 126.4 | 127.5 | 127.7 | 126.1 | 125.2 | 126.1 | 126.1 | 126.1 | 125 | 125 | 125 | 125 | 127.4 | 126.3 | 125.8 | 127 | 129.2 | 130 | 127.9 | 127.4 | 128.2 |  | 130 | 125
SUI 132KV | 131.6 | 132 | 132.1 | 132.1 | 131 | 130.5 | 132.1 | 130.2 | 129 | 129.3 | 127.4 | 128.5 | 128.9 | 127.4 | 127.3 | 128.1 | 128.7 | 128.7 | 127 | 127 | 127 | 127 | 129 | 127.3 | 127.7 | 128.7 | 131.7 | 131.4 | 129.5 | 130.7 | 131.8 |  | 132.1 | 127
DUBI 132KV | 129 | 131.8 | 131.6 | 127.5 | 127.8 | 127.5 | 127 | 128.3 | 126.4 | 130.5 | 126.2 | 131.4 | 129.9 | 126.5 | 127 | 128.4 | 130.5 | 130.5 | 128 | 128 | 128 | 128 | 130.1 | 129.6 |  |  | 131.4 | 130 | 126.7 | 130.6 | 129.7 |  | 131.8 | 126.2
ANAMANI 132KV | 131.2 | 133.5 | 133.6 | 131 | 131.1 | 130.7 | 130.1 | 130.4 | 129.7 | 132.9 | 128 | 131.9 | 130.2 | 127.8 | 127.7 | 129.4 | 133.1 | 133.1 | 130 | 130 | 130 | 130 | 127.8 | 128.9 |  |  | 132.9 | 131.9 | 129.8 | 133.6 | 133.9 |  | 133.9 | 127.7
KG-A 132KV | 132 | 132.8 | 131.6 | 130.8 | 130 | 131.2 | 133.6 | 132 | 134.1 | 134.6 | 134.3 | 134 | 133.4 | 132.4 | 133.6 | 133.5 | 133.4 | 133.4 | 132 | 132 | 132 | 132 | 133.6 | 134 | 133.8 | 134.8 | 136.9 | 136.7 | 135.5 | 134.1 | 134.3 |  | 136.9 | 130
KOHALPUR 132KV | 135.1 | 125.8 | 125.5 | 127 | 127.6 | 129.2 | 124.4 | 127.3 | 135.8 | 134.5 | 130.5 | 128.8 | 130.8 | 130.4 | 127.3 | 130.9 | 133.3 | 133.3 | 127 | 127 | 127 | 127 | 132 | 129.2 | 131 | 134.7 | 135.3 | 134.6 | 134.3 | 133.8 | 130.2 |  | 135.8 | 124.4
SUI 66KV | 66.2 | 66.5 | 66.7 | 66.7 | 66.2 | 66 | 66.7 | 65.7 | 64.6 | 65.1 | 63.9 | 64.3 | 64.5 | 63.6 | 63.7 | 64 | 64.3 | 64.3 | 64.3 | 64.3 | 64.3 | 64.3 | 64.8 | 63.9 | 64.3 | 65.8 | 65.8 | 65.6 | 64.9 | 65..6 | 66.2 |  | 66.7 | 63.6
[33 empty] | 0 | 0
Kathmandu Load | 149.097 | 147.899 | 136.813 | 140.54 | 141.648 | 176.328 | 203.748 | 239.692 | 307.191 | 349.16 | 384.424 | 367.54 | 352.44 | 362.72 | 42 | 328.52 | 322.96 | 318.96 | 294.54 | 291.54 | 314.151 | 313.151 | 363.653 | 445.9 | 449.261 | 417.153 | 384.525 | 370.14 | 351.34 | 254.54 | 197.86 |  | 449.261 | 42
MRS-SYU | 4.7 | 2.8 | -1.3 | -21.1 | -22.4 | -15.6 | 3.1 | 6.7 | 18 | 24.8 | 40.6 | 42.5 | 35.4 | 29.4 | 40.2 | 36.8 | 35.3 | 35.3 | 26 | 24 | 14.3 | 14.3 | 20.4 | 40.4 | 43.3 | 41.9 | 33.7 | 35.8 | 33 | 23.6 | 18.2 | 75 | 43.3 | -22.4
NMRS-MATA | 1.4 | 1.1 | -6.1 | -33.7 | -34.4 | -24.4 | 1.3 | 7.3 | 21.3 | 35.1 | 55.7 | 59.3 | 48 | 40.4 | 48.6 | 43.4 | 41.9 | 41.9 | 28 | 25 | 13.1 | 13.1 | 28.3 | 53.2 | 57.4 | 56.5 | 45.1 | 47.4 | 40.4 | 26.6 | 20.7 | 240 | 59.3 | -34.4
KL2-MATA | -39 | -39.7 | -38.7 | -9.5 | -9.9 | -6.3 | -1.8 | 6 | 19.4 | 32.2 | 35 | 33 | 35 | 39 | 22.8 | 14.3 | 15.6 | 15.6 | 18 | 23 | 42 | 42 | 50 | 61 | 58.2 | 48 | 48 | 47 | 39 | -8 | -28 | 240 | 61 | -39.7
KL1-SYU | -18 | -18.8 | -5.9 | -3.6 | -3.7 | -0.9 | 5.6 | 8.4 | 11.8 | 25.9 | 27.9 | 24.9 | 24.2 | 26.4 | 12.5 | 10.3 | 7.9 | 8.9 | 8 | 12 | 22.1 | 22.1 | 25.6 | 31.1 | 31 | 29.4 | 27.5 | 26 | 17 | 8 | 1.5 | 60 | 31.1 | -18.8
KHIMTI-LAMOSANGHU | 112.057 | 113.059 | 103.373 | 123 | 126.608 | 138.088 | 110.208 | 125.952 | 150.552 | 144.32 | 136.284 | 114.8 | 114.8 | 126.28 | 127.92 | 118.08 | 119.72 | 119.72 | 120 | 120 | 139.111 | 139.111 | 156.813 | 167 | 164.161 | 156.813 | 145.885 | 129.6 | 137.6 | 116.8 | 97.92 | 120 | 167 | 97.92
LAMOSHANGU-BHAKTAPUR | 79.4 | 79.2 | 77.8 | 85.9 | 86.6 | 92.2 | 78.9 | 86.5 | 97.1 | 95.6 | 89.4 | 79 | 78.9 | 84.5 | 85 | 81 | 81.1 | 81.1 | 88 | 93 | 93.3 | 93.3 | 101 | 104.1 | 102.2 | 98.9 | 96.2 | 90 | 92 | 84 | 76
BALAJU-SYUCHATAR | 58 | 64.8 | 68.1 | 28.7 | 27.8 | 77 | 40.4 | 35.5 | 20.1 | -10.7 | -28.5 | -38 | -28.8 | -14.6 | -5.1 | -2 | 5 | 5 | 20 | 22 | 15.5 | 15.5 | 0.2 | -33.9 | -39.7 | -28.6 | -26 | -27 | -13.2 | 31 | 43.2
DHALKE-NAWALPUR I | 100.5 | 98.9 | 101.4 | 84.6 | 83.3 | 96.1 | 72.6 | 80.3 | 92.1 | 79.1 | 66.8 | 55.3 | 59.4 | 72.6 | 74.6 | 69.6 | 71.7 | 71.7 | 78 | 85 | 80 | 80 | 85.9 | 78.8 |  | 67.8 | 76.3 | 79.3 | 72 | 91 | 86 |  | 101.4 | 55.3
N. BHARATPUR-BARDGHAT I | 16.8 | 19.2 | 22.3 | 47.9 | 48.3 | 55.6 | 31.6 | 32.8 | 24.5 | 12.5 | -4.9 | -6.8 | -5.2 | -1.2 | -7.7 | -6.4 | -8.4 | -8.4 | -2 | 0 | 4.6 | 4.6 | 4.4 | -10.2 | -11.6 | -6.5 | -4.8 | 0 | 0 | 12 | 14 |  | 55.6 | -11.6
DAMAK-DUHABI | -3.7 | -4.2 | -2.7 | -2.7 | -1.6 | -5.3 | -9.3 | -18.1 | -28.8 | -31.3 | -33.4 | -33 | -26.3 | -19.3 | -25.9 | -24.9 | -15.6 | -15.6 | -11 | -11 | -30.1 | -30.1 | -49.6 | -54.6 |  |  | -30.7 | -27 | -23 | -13 | -10 |  | -1.6 | -54.6
HETAUDA-KAMANE | 20.2 | 19.2 | 17.2 | 18.5 | 19 | 22 | 23.3 | 25 | 22.1 | 12.2 | 12.7 | 12.7 | 12.9 | 8.8 | 20.5 | 25.2 | 24.2 | 24.2 | 24 | 26 | 10.9 | 10.9 | 10.1 | 11.6 | 11 | 10.7 | 8 | 17 | 17 | 15 | 21 |  | 26 | 8
MIRCHAIYA LAHAN 2 | 85.6 | 82.1 | 79.1 | 81.4 | 77.7 | 83.5 | 83.9 | 88.3 | 98 | 92.9 | 95.6 | 74.4 | 66.5 | 91.2 | 104.8 | 102.74 | 93.3 | 93.3 | 96 | 96 | 75.3 | 75.3 | 88.6 | 102.3 |  | 86.5 | 91.2 | 96.4 | 107 | 101.2 | 87 |  | 107 | 66.5
Water Level
UTK | 1984.35 | 1984.6 | 1984.8 | 1985 | 1985.22 | 1895.42 |  | 1985.62 |  | 1985.64 |  | 1985.1 | 1984.65 | 1984.71 | 1984.77 | 1984.85 | 1985.01 | 1985.22 | 1985.4 | 1985.6 | 1985.65 |  | 1985.76 |  | 1985.4 |  | 1984.8 |  | 1984.63 | 1984.6 | 1984.78
KGA | 521.7 | 521.8 | 521.94 | 522.12 | 522.4 | 522.7 |  | 522.74 |  | 522.56 |  | 522.24 | 521.96 | 521.88 | 521.8 | 521.65 | 521.6 | 521.58 | 521.52 | 521.46 | 521.4 |  | 521.46 |  | 521.05 |  | 520.51 |  | 520.28 | 519.92 | 519.73
MMRS | 623.2 | 623.7 | 624.07 | 624.35 | 624.55 | 624.78 |  | 624.62 |  | 624 |  | 623.19 | 622.72 | 622.64 | 622.55 | 622.4 | 622.32 | 622.214 | 622.2 | 622.25 | 622.5 |  | 622.81 |  | 622.8 |  | 622.75 |  | 622.73 | 622.59 | 622.48
MRS | 335.61 | 335.9 | 336.11 | 336.35 | 336.6 | 336.82 |  | 336.89 |  | 336.86 |  | 336.56 | 336.25 | 335.9 | 335.49 | 335.49 | 335.71 | 335.89 | 335.91 | 335.92 | 335.95 |  | 336.05 |  | 335.9 |  | 335.54 |  | 335.38 | 334.96 | 334.76
CHM | 884.9 | 885.6 | 886 | 886.7 | 887 | 887.4 |  | 886.9 |  | 886 |  | 885 | 884.1 | 884.5 | 885.1 | 885.1 | 884.7 | 884.3 | 884.1 | 883.9 | 883.8 |  | 884.4 |  | 883.6 |  | 882.9 | 882.8 | 882.7 | 882.5 | 883
KL 1 | 0: 1519.3; 0.58333: 1519.33; 0.79167: 1519.34
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1677.29; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/11)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 12
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/12 |  |  | 2080/10/12 |  |  | Saturday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 531.4 | 539.6 | 530.9 | 530.7 | 564 | 576.7 | 560.6 | 597.7 | 451.3 | 303.5 | 223 | 294.3 | 461.3 | 488.9 | 553 | 599 | 534.4 | 610 | 588.1 | 619.8 | 598.2 | 606 | 460.1 | 284.7 | 297.4 | 370.8 | 471.3 | 480.2 | 553.2 | 560.5 | 560
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1681MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1147 | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1282.99 | 1335.29 | 1415.79 | 1511.69 | 1671.09 | 1681.29 | 1671.59 | 1499.49 | 1429.69 | 1317.39 | 1356.19 | 1328.29 | 1352.99 | 1295.99 | 1321.99 | 1304.49 | 1490.49 | 1635.15 | 1773.25 | 1720.99 | 1700.09 | 1650.19 | 1591.29 | 1259.29 | 1202.09
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.5 | 27.5 | 26.6 | 27.2 | 27.2 | 86 | 27.8 | 25.7
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 12
Super Dordi (54) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 54 | 11 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/12)
Likhu-IV(52.4) | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7 | 15.1 | 15.2 | 15.2 | 52.4 | 15.8 | 14.7
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 28.6 | 28.6 | 50 | 29 | 25 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 15.8 | 15.8 | 15.8 | 45 | 17.6 | 15.1 |  | IPP | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 478.25 | 452.25 | 452.25 | 477.15 | 477.15 | 477.15 | 474.45 | 473.45 | 474.35 | 468.05 | 468.05 | 468.05 | 476.05 | 477.75 | 478.05 | 478.05
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 0 |  | NEA SUB | 42.2 | 42.2 | 35.6 | 35.6 | 35.6 | 50.6 | 65.6 | 145.7 | 397.2 | 287.2 | 52.2 | 35.2 | 35.2 | 35.2 | 65.2 | 65.2 | 35.2 | 50.2 | 65.2 | 430.2 | 342.2 | 175.2 | 50.2 | 35.2
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7 |  | NEA ROR PROR | 152.54 | 106.24 | 103.54 | 103.64 | 127.84 | 147.84 | 231.74 | 257.34 | 282.84 | 317.84 | 283.74 | 278.44 | 253.04 | 164.84 | 174.24 | 124.34 | 118.34 | 103.94 | 151.24 | 340.3 | 261.04 | 209.14 | 179.84 | 128.34
Upper Chameliya(40) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 13 | 11.8 |  | IMPORT | 560 | 531.4 | 539.6 | 530.9 | 530.7 | 564 | 560.6 | 451.3 | 223 | 294.3 | 461.3 | 488.9 | 553 | 599 | 534.4 | 610 | 588.1 | 619.8 | 606 | 284.7 | 370.8 | 480.2 | 553.2 | 560.5
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 300 | 320 | 250 | 150 | 0 | 80 | 80 | 80 | 80 | 80 | 200 | 250 | 250 | 250 | 0 | 0
Nyadi(30) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.6 |  | System_Load | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1335.29 | 1511.69 | 1681.29 | 1671.59 | 1499.49 | 1429.69 | 1318.39 | 1356.19 | 1328.29 | 1352.99 | 1295.99 | 1321.99 | 1490.49 | 1773.25 | 1700.09 | 1592.29 | 1261.29 | 1202.09
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 6.2 | 6.2 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -2 | 0
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.3 | 7.3 | 28 | 7.3 | 7.2 |  | National_Load | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1335.29 | 1511.69 | 1681.29 | 1671.59 | 1499.49 | 1429.69 | 1317.39 | 1356.19 | 1328.29 | 1352.99 | 1295.99 | 1321.99 | 1490.49 | 1773.25 | 1700.09 | 1591.29 | 1259.29 | 1202.09
Dordi(27) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 30 | 6.3 | 0
Upper Madi(25) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.4 | 8.4 | 8.4 | 25 | 10 | 0
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 6.9 | 6.9 | 6.9 | 25 | 8.2 | 6.9
Solu Khola(23.5) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.8 | 7.8 | 7.8 | 23.5 | 7.8 | 7.3
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12.5 | 12.5 | 12.5 | 22 | 12.5 | 11
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | [11 empty] | 18.1 | 12 | 24.1 | 25 | 25 | 26 | 22.3 | 22.3 | 22.3 | 21.2 | 21.4 | 19.8 | 18.6 | 17.3 | 17.3 | 17.2 | 16.2 | 17.6 | 19.7 | 19.5 | 240 | 26 | 12
Total IPP | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 477.35 | 478.25 | 452.25 | 452.25 | 477.15 | 477.15 | 477.15 | 474.45 | 473.45 | 474.35 | 468.05 | 468.05 | 468.05 | 468.05 | 468.05 | 468.05 | 476.05 | 476.05 | 477.75 | 478.05 | 478.05 | 1042.4 | 478.25 | 452.25
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 30 | 50 | 110 | 340 | 360 | 250 | 15 | 0 | 0 | 0 | 30 | 30 | 0 | 15 | 0 | 30 | 200 | 395 | 400 | 300 | 180 | 140 | 15 | 0 | 456 | 400 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 15.2 | 15.2 | 8.6 | 8.6 | 8.6 | 8.6 | 8.7 | 8.6 | 8.6 | 8.7 | 10.2 | 10.2 | 10.2 | 10.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 15.2 | 8.1 | 8.2 | 8.2 | 8.2 | 22.1 | 15.2 | 8.1
Total NEA SUBSIDIARIES | 42.2 | 42.2 | 35.6 | 35.6 | 35.6 | 50.6 | 50.7 | 65.6 | 85.6 | 145.7 | 377.2 | 397.2 | 287.2 | 52.2 | 35.2 | 35.2 | 35.2 | 65.2 | 65.2 | 35.2 | 50.2 | 35.2 | 65.2 | 235.2 | 430.2 | 435.2 | 342.2 | 215.1 | 175.2 | 50.2 | 35.2 | 538.1 | 435.2 | 35.2
KGA(144) | 30.3 | 0 | 0 | 0 | 0 | 0 | 30.1 | 62.7 | 61.2 | 80 | 81.5 | 81.5 | 112.2 | 101.2 | 91.6 | 91.6 | 31.3 | 31.3 | 0 | 0 | 0 | 0 | 30.6 | 30.6 | 136.2 | 81.2 | 81.6 | 81.4 | 61.5 | 30 | 0 | 144 | 136.2 | 0
Middle MRS(70) | 26 | 26 | 26.5 | 26.6 | 35 | 34.7 | 34.8 | 34.8 | 34.8 | 34.8 | 35.3 | 35.3 | 35.3 | 22.1 | 22 | 22 | 25.1 | 25.1 | 24.8 | 24.8 | 24.8 | 24.8 | 24.6 | 35 | 35 | 34.8 | 34.8 | 25 | 24.9 | 24.6 | 25 | 70 | 35.3 | 22
MRS(69) | 16 | 0 | 0.8 | 0.8 | 16.6 | 36.7 | 37.1 | 47 | 65.2 | 53.4 | 51.5 | 65.8 | 65.4 | 52.5 | 52.5 | 32 | 16.8 | 16 | 0 | 0 | 0 | 0 | 18.9 | 69 | 64 | 49.2 | 44.3 | 44 | 44.5 | 44.3 | 22.7 | 69 | 69 | 0
U Trisuli 3A(60) | 40.3 | 40.3 | 36.3 | 36.3 | 36.3 | 36.5 | 36.3 | 37.3 | 39 | 38.5 | 38 | 37.8 | 38 | 36.3 | 36.3 | 36.3 | 37.3 | 37.3 | 35 | 35 | 35 | 35 | 34.3 | 34.3 | 34.3 | 34.5 | 34.5 | 34.5 | 36 | 38.3 | 38 | 60 | 40.3 | 34.3
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 10.3 | 15 | 15 | 15 | 14.8 | 14.9 | 10 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 10.1 | 28 | 27.8 | 23 | 10 | 0 | 0 | 0 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 1.8 | 6.2 | 10.5 | 15.4 | 18.3 | 18.3 | 11.5 | 11.7 | 11.7 | 5.7 | 1.3 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.3 | 0
TRI(24) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 14
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 10 | 10 | 10 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 9.8 | 10.2 | 10.2 | 14.1 | 10.4 | 8.7
MODI(14) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 14 | 3.4 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 3.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.5
Total ROR | 152.54 | 106.24 | 103.54 | 103.64 | 127.84 | 147.84 | 178.24 | 231.74 | 255.14 | 257.34 | 263.04 | 282.84 | 317.84 | 283.74 | 278.44 | 253.04 | 164.84 | 174.24 | 124.34 | 118.34 | 103.94 | 103.04 | 151.24 | 221.8 | 340.3 | 270.34 | 261.04 | 237.74 | 209.14 | 179.84 | 128.34 | 489.91 | 340.3 | 103.04
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 48 | 63 | 68.2 | 56.3 | 54.5 | 55 | 67.3 | 68.2 | 56.6 | 64 | 64.8 | 59 | 58 | 60.2 | 60 | 55 | 55.3 | 54 | 78 | 71 | 60.4 | 64.7 | 68 | 69.1 | 53.2 | 48.1 | 50.6 | 63.6 | 67 | 61.5 | 60.9 |  | 78 | 48
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 405 | 378 | 378.2 | 374.5 | 395.4 | 405.6 | 419.9 | 397.4 | 420.2 | 295 | 145 | 87 | 158 | 341.7 | 376.9 | 410 | 466.9 | 393 | 404 | 432 | 432 | 410 | 419 | 236 | 83 | 90 | 174 | 254 | 255 | 306 | 400 |  | 466.9 | 83
RAMNAGAR | 3 | 25 | 22.2 | 26.7 | 33 | 32.9 | 26.5 | 27 | 25 | 15 | 15 | 15 | 10 | 13 | 22 | 40 | 30.3 | 45 | 47 | 41 | 18 | 3 | 20 | 25 | 28 | 25 | 20 | 20 | 21 | 40 | 38 |  | 47 | 3
RAXAUL 132 | 27 | 14 | 24 | 22.6 | 0 | 21.4 | 21.2 | 20.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.2 | 0 | 73 | 84 | 67 | 96 | 90.2 | 100.2 | 90 | 98 | 98 | 98.6 | 19 |  | 100.2 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 77 | 51.4 | 47 | 50.8 | 47.8 | 49.1 | 41.8 | 47.6 | 74.7 | 77.3 | 78.7 | 62 | 68.3 | 46.4 | 30 | 48 | 46.5 | 42.4 | 41.8 | 44.1 | 36.4 | 36.5 | 32 | 34 | 30.3 | 34.1 | 36.2 | 35.7 | 39.2 | 47.1 | 42.6 |  | 78.7 | 30
Total IMPORT | 560 | 531.4 | 539.6 | 530.9 | 530.7 | 564 | 576.7 | 560.6 | 597.7 | 451.3 | 303.5 | 223 | 294.3 | 461.3 | 488.9 | 553 | 599 | 534.4 | 610 | 588.1 | 619.8 | 598.2 | 606 | 460.1 | 284.7 | 297.4 | 370.8 | 471.3 | 480.2 | 553.2 | 560.5 | 0 | 619.8 | 223
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1282.99 | 1335.29 | 1415.79 | 1331.69 | 1421.09 | 1381.29 | 1351.59 | 1249.49 | 1279.69 | 1318.39 | 1276.19 | 1248.29 | 1272.99 | 1215.99 | 1241.99 | 1204.49 | 1290.49 | 1385.15 | 1523.25 | 1470.99 | 1450.09 | 1400.19 | 1342.29 | 1261.29 | 1202.09 | 2231.81 | 1523.25 | 1147.49
Interruption/Tripping | [9 empty] | 180 | 250 | 300 | 320 | 250 | 150 | 0 | 80 | 80 | 80 | 80 | 80 | 100 | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 0 |  |  | 320 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1282.99 | 1335.29 | 1415.79 | 1511.69 | 1671.09 | 1681.29 | 1671.59 | 1499.49 | 1429.69 | 1318.39 | 1356.19 | 1328.29 | 1352.99 | 1295.99 | 1321.99 | 1304.49 | 1490.49 | 1635.15 | 1773.25 | 1720.99 | 1700.09 | 1650.19 | 1592.29 | 1261.29 | 1202.09 | 1693.71 | 1773.25 | 1147.49
TOTAL NATIONAL LOAD (ACTUAL) | 1232.09 | 1157.19 | 1156.09 | 1147.49 | 1171.49 | 1239.79 | 1282.99 | 1335.29 | 1415.79 | 1511.69 | 1671.09 | 1681.29 | 1671.59 | 1499.49 | 1429.69 | 1317.39 | 1356.19 | 1328.29 | 1352.99 | 1295.99 | 1321.99 | 1304.49 | 1490.49 | 1635.15 | 1773.25 | 1720.99 | 1700.09 | 1650.19 | 1591.29 | 1259.29 | 1202.09 |  | 1773.25 | 1147.49
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 |  | 2 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 |  | 2 | 0
NET IMPORT | 560 | 531.4 | 539.6 | 530.9 | 530.7 | 564 | 576.7 | 560.6 | 597.7 | 451.3 | 303.5 | 223 | 294.3 | 461.3 | 488.9 | 552 | 599 | 534.4 | 610 | 588.1 | 619.8 | 598.2 | 606 | 460.1 | 284.7 | 297.4 | 370.8 | 471.3 | 479.2 | 551.2 | 560.5 |  | 619.8 | 223
HZ | 50.032 | 49.992 | 50.038 | 50 | 50.016 | 49.905 | 49.984 | 49.983 | 50.075 | 50.075 | 49.985 | 50.07 | 49.878 | 49.991 | 50.031 | 50.01 | 50.002 | 50.045 | 49.985 | 49.878 | 50.078 | 50.159 | 49.98 | 49.913 | 49.924 | 50.045 | 50.013 | 49.966 | 49.9 | 49.94 | 49.99 |  | 50.159 | 49.878
HTD 132KV | 128 | 129.5 | 128.7 | 128 | 127 | 128.7 | 130 | 128.8 | 128.6 | 128.6 | 127 | 125.9 | 125.4 | 127.3 | 126.4 | 125 | 124.9 | 126.3 | 126.3 | 127.4 | 130.4 | 127 | 127.5 | 126.6 | 128.5 | 128.5 | 128.9 | 130.1 | 131.1 | 130.7 | 128 |  | 131.1 | 124.9
SUI 132KV | 132 | 133.78 | 133.2 | 132.6 | 131.3 | 132.3 | 132.8 | 131.6 | 130.7 | 130.7 | 129.1 | 127.8 | 127.4 | 128.8 | 129 | 128 | 127.5 | 129.2 | 129.2 | 129.6 | 132.4 | 129.1 | 129.1 | 128.1 | 130.3 | 130.7 | 130.8 | 131.8 | 132.8 | 132.9 | 131.4 |  | 133.78 | 127.4
DUBI 132KV | 128 | 130 | 128.1 | 127.1 | 130.3 | 130.7 | 130.3 | 128.8 | 124.8 | 124.8 | 131.1 | 128.4 | 129.7 | 132 | 126.3 | 128.5 | 128.7 | 127.2 | 127.2 | 127.9 | 131.7 | 130.7 | 127.6 | 127.4 | 129.4 | 131.6 | 130.2 | 132.2 | 129.9 | 128.5 | 129.9 |  | 132.2 | 124.8
ANAMANI 132KV | 132 | 133.7 | 130.9 | 129.2 | 132 | 132.4 | 132.6 | 130.6 | 126.4 | 126.4 | 131.6 | 128.2 | 129.4 | 132.8 | 126.2 | 130.8 | 131.2 | 131 | 131 | 131.1 | 132.8 | 132.9 | 128.6 | 128.3 | 130.9 | 133.7 | 132.6 | 134.8 | 132.8 | 132.2 | 134.1 |  | 134.8 | 126.2
KG-A 132KV | 134 | 136.4 | 136.8 | 134.3 | 131 | 131 | 134 | 132.9 | 134.1 | 134.1 | 134.6 | 133.4 | 133.5 | 135.6 | 134 | 132 | 130.4 | 132.6 | 132.6 | 132.7 | 136.9 | 133.3 | 135.1 | 135.6 | 135.6 | 136.8 | 135.3 | 135.6 | 136.1 | 133.6 | 131.3 |  | 136.9 | 130.4
KOHALPUR 132KV | 135 | 130.8 | 134.9 | 129.9 | 132.2 | 133.5 | 124.8 | 125.3 | 129.5 | 129.5 | 126.8 | 128.8 | 126.1 | 133.6 | 133.2 | 132 | 131.6 | 127.8 | 127.8 | 128.8 | 125.9 | 131.7 | 130.2 | 132.4 | 131.9 | 135 | 134.1 | 134.8 | 135 | 133.3 | 134 |  | 135 | 124.8
SUI 66KV | 66.4 | 67 | 66.8 | 66.9 | 66.1 | 66.6 | 66.8 | 66.3 | 65.2 | 65.2 | 64.8 | 64.3 | 64.3 | 65.1 | 65 | 64.6 | 64 | 65.4 | 64.9 | 65.6 | 66.8 | 64.8 | 64.7 | 64.1 | 65.2 | 65.3 | 65.4 | 66 | 66.6 | 67 | 66.1 |  | 67 | 64
[33 empty] | 0 | 0
Kathmandu Load | 164.24 | 145.92 | 139.618 | 137.403 | 140.916 | 168.478 | 194.274 | 226.656 | 273.859 | 273.759 | 322.78 | 367.893 | 367.279 | 356.95 | 42 | 42 | 298.281 | 265.36 | 264.14 | 254.52 | 256.24 | 292.42 | 343.5 | 393.12 | 426.7 | 398 | 386.96 | 365.94 | 330.06 | 272 | 188.08 |  | 426.7 | 42
MRS-SYU | 7.6 | 7 | 3.1 | 2.5 | 3 | 5.5 | 10.1 | 17.8 | 23.9 | 23.9 | 31.2 | 37.5 | 39.6 | 35.4 | 34.1 | 31 | -9.1 | -4.3 | -21.2 | -2.4 | -3 | -2.2 | 15.6 | 33 | 35.1 | 23.1 | 26.6 | 26.9 | 25.6 | 19.1 | 1.1 | 75 | 39.6 | -21.2
NMRS-MATA | 7.8 | 6 | 1.1 | 0.2 | 1.2 | 3.2 | 8.9 | 18.4 | 25.1 | 25.1 | 42.9 | 50 | 52.8 | 46.9 | 40.9 | 26.5 | -19.3 | -12.2 | -35 | -9 | -3 | -1.6 | 19.5 | 42.4 | 47 | 28.7 | 36.1 | 36.4 | 30.1 | 19.1 | -3.1 | 240 | 52.8 | -35
KL2-MATA | -35 | -41 | -40.1 | -40 | -44.9 | -33.6 | -23.5 | -16.5 | -5.1 | -5.1 | 15.4 | 23 | 20.2 | 30 | 15.8 | 3 | 53 | 36 | 57.9 | 23.4 | 31 | 43 | 48 | 50 | 56 | 76 | 62.5 | 55 | 53.2 | 45.8 | -14.1 | 240 | 76 | -44.9
KL1-SYU | -4.5 | -5.3 | -6.8 | -6.8 | -8.2 | -8.7 | -1.8 | 3.1 | 11.2 | 11.2 | 19.1 | 21.4 | 21.2 | 22.5 | 19.4 | 17 | 20.8 | 17 | 18.8 | 14.6 | 17 | 23.4 | 26.4 | 28 | 30 | 32 | 30 | 29 | 27.5 | 23 | 8.6 | 60 | 32 | -8.7
KHIMTI-LAMOSANGHU | 100.8 | 91.68 | 98.778 | 97.963 | 106.276 | 118.338 | 117.034 | 119.316 | 132.519 | 132.519 | 127.14 | 143.453 | 136.439 | 121.91 | 117.234 | 100 | 154.141 | 129.92 | 147 | 137.28 | 128 | 144.48 | 149.76 | 145.92 | 164.8 | 153.76 | 144.32 | 131.2 | 105.12 | 73.76 | 104.64 | 120 | 164.8 | 73.76
LAMOSHANGU-BHAKTAPUR | 74 | 71 | 73.3 | 72.5 | 76 | 82.3 | 81.3 | 82.1 | 88.6 | 88.6 | 86.5 | 92.5 | 88.6 | 81.5 | 79.2 | 85 | 97.2 | 89 | 94.8 | 93.1 | 89.1 | 97 | 100 | 97.3 | 107 | 100 | 93.7 | 88 | 76.7 | 60.9 | 76.8
BALAJU-SYUCHATAR | 61 | 67 | 74.3 | 72.8 | 65.9 | 63.7 | 50.5 | 36 | 24.1 | 24.1 | -4.2 | -12.2 | -17.2 | -14.4 | 0.1 | 21 | 47.5 | 46 | 59.2 | 50 | 31.4 | 29 | 5 | -27 | -27 | -25.3 | -25.9 | -24 | -21.6 | -17.3 | 60
DHALKE-NAWALPUR I | 91 | 82 | 89.7 | 87.5 | 98.3 | 97.7 | 97.2 | 96.5 | 103 | 103 | 79.1 | 85.5 | 78.4 | 82 | 87.8 | 94 | 89.8 | 81 | 87 | 83 | 76 | 90 | 80 | 71 | 77 | 92 | 92 | 78 | 78.9 | 61.3 | 95.8 |  | 103 | 61.3
N. BHARATPUR-BARDGHAT I | 15 | 5 | 18.4 | 22.2 | 29.2 | 35.4 | 21.8 | 8.2 | 4.2 | 4.2 | -23.4 | -11.7 | -15.9 | -14.2 | -4.7 | 0 | 34 | 20 | 14.3 | 16 | 17 | 20 | 13 | -2.2 | -2 | 8.1 | 5.6 | 0 | 4.1 | 10.9 | 19.8 |  | 35.4 | -23.4
DAMAK-DUHABI | -9 | -6 | -4.7 | -3.2 | -4.6 | -7.1 | -12.4 | -16.3 | -22.6 | -22.6 | -37.9 | -40.2 | -40.3 | -19.8 | -11.4 | -15 | -9.2 | -10 | -12.6 | -14.8 | -29 | -29 | -41 | -46 | -39 | -35 | -31.3 | -28 | -21.9 | -15.1 | -10.7 |  | -3.2 | -46
HETAUDA-KAMANE | 21 | 21.4 | 21.3 | 20.5 | 20.4 | 21.5 | 21.7 | 22.5 | 22.8 | 22.8 | 8.4 | 8.5 | 8.6 | 7.4 | 7.9 | 20 | 20.2 | 21 | 20.5 | 15.9 | 6 | 7.4 | 9 | 9.5 | 10 | 8.7 | 8.3 | 8.4 | 40.3 | 24.2 | -7.8 |  | 40.3 | -7.8
MIRCHAIYA LAHAN 2 | 94 | 90 | 82.3 | 77.8 | 78.9 | 86.1 | 82.7 | 84.4 | 92.1 | 92.1 | 75.8 | 78.8 | 72.3 | 60 | 63.6 | 71 | 85.8 | 81.3 | 83.7 | 81.7 | 78.01 | 78 | 96 | 105 | 101 | 94.1 | 89.4 | 88.5 | 95.4 | 94.2 | 85.9 |  | 105 | 60
Water Level
UTK | 1984.94 | 1985.17 | 1985.39 | 1985.6 | 1985.75 | 1985.97 |  | 1986.08 |  | 1986.05 |  | 1985.32 | 1984.8 | 1984.52 | 1984.8 | 1984.88 | 1985.05 | 1985.12 | 1985.23 | 1985.3 | 1985.42 | 1985.5 | 1985.55 |  | 1985.1 |  | 1984.25 |  | 1983.9 | 1983.8 | 1984.04
KGA | 519.87 | 520.1 | 520.46 | 520.78 | 521.14 | .521.48 |  | 521.62 |  | 521.52 |  | 521.36 | 521.14 | 520.72 | 520.4 | 520.12 | 519.93 | 520.05 | 520.36 | 520.77 | 521.1 |  | 521.37 |  | 521.08 |  | 520.7 |  | 520.52 | 520.5 | 520.78 | 1905-06-06 07:12
MMRS | 622.52 | 622.51 | 622.58 | 522.57 | 622.62 | 622.54 |  | 622.44 |  | 622.34 |  | 622.2 | 622.21 | 622.22 | 622.32 | 622.27 | 622.24 | 622.3 | 622.37 | 622.41 | 622.44 |  | 622.35 |  | 622.2 |  | 621.99 |  | 621.96 | 621.92 | 621.91
MRS | 334.72 | 334.78 | 335.14 | 335.4 | 335.75 | 335.94 |  | 335.88 |  | 335.62 |  | 335.37 | 334.97 | 334.71 | 334.51 | 334.42 | 334.45 | 334.64 | 334.97 | 335.28 | 335.52 |  | 335.75 |  | 335.62 |  |  |  | 335.16 | 335.02 | 335.03
CHM | 883.5 | 884.3 | 884.9 | 885.6 | 886.1 | 886.6 |  | 886.8 |  | 886.7 |  | 886.5 | 886.2 | 885.9 | 885.6 | 885.3 | 885.6 | 885.7 | 885.6 | 885.5 | 885.4 |  | 885.7 |  | 885.4 |  | 883.9 |  | 884 | 884.7 | 885.2
KL 1 | 0.33333: 1519.36; 0.625: 1519.38
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1681.29; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/12)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 13
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/13 |  |  | 2080/10/13 |  |  | Sunday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 519.3 | 492.1 | 501.1 | 525.3 | 531.6 | 574 | 590 | 575.7 | 547.8 | 346.1 | 251.6 | 521.3 | 519.6 | 545.3 | 682.9 | 660.32 | 701.8 | 691.2 | 679.7 | 641.9 | 582.2 | 606.8 | 655.2 | 631.9 | 646.1 | 645.5 | 673.1 | 656.1 | 652 | 632 | 556.2
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1833MW at 9:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1112 | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1341.39 | 1388.79 | 1483.79 | 1649.49 | 1667.09 | 1581.39 | 1832.89 | 1553.59 | 1581.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1528.39 | 1699.09 | 1853.65 | 1877.35 | 1779.69 | 1726.89 | 1627.49 | 1474.49 | 1378.39 | 1270.09
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW)
Solu Khola Dudhkoshi(86) | 29.5 | 29.5 | 29.5 | 28.8 | 26.9 | 27.5 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 86 | 29.5 | 26.9
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 13
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/13)
Likhu-IV(52.4) | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 52.4 | 15.2 | 15.2
Upper Marsyangdi "A"(50) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 50 | 28.6 | 28.6 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 45 | 15.8 | 15.8 |  | IPP | 480.35 | 480.35 | 480.35 | 479.65 | 477.75 | 478.35 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.1 | 35.1 | 35.1 | 35.1 | 35 | 35.2 | 35.1 | 96.2 | 306.2 | 286.2 | 51.2 | 51.2 | 86.2 | 112.2 | 90.1 | 75.2 | 110.1 | 122.1 | 181.2 | 191.1 | 171.1 | 115.1 | 75.1 | 35.1
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7.5 |  | NEA ROR PROR | 105.64 | 103.44 | 104.04 | 104.04 | 101.94 | 199.14 | 285.94 | 277.74 | 265.84 | 267.64 | 225.04 | 226.94 | 257.84 | 257.84 | 256.84 | 269.14 | 217.14 | 152.34 | 183.24 | 326.5 | 232.44 | 227.44 | 176.44 | 129.14
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 556.2 | 519.3 | 492.1 | 501.1 | 525.3 | 531.6 | 590 | 547.8 | 251.6 | 521.3 | 519.6 | 545.3 | 682.9 | 660.32 | 701.8 | 691.2 | 679.7 | 641.9 | 606.8 | 631.9 | 645.5 | 656.1 | 652 | 632
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 280 | 280 | 280 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 250 | 200 | 0 | 0 | 0
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8 |  | System_Load | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1388.79 | 1649.49 | 1581.39 | 1832.89 | 1553.59 | 1581.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1699.09 | 1877.35 | 1726.89 | 1476.49 | 1381.39 | 1274.09
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 6.2 | 6.2 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2 | -3 | -4
Lower Likhu(28) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 28 | 7.3 | 7.3 |  | National_Load | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1388.79 | 1649.49 | 1581.39 | 1832.89 | 1553.59 | 1581.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1699.09 | 1877.35 | 1726.89 | 1474.49 | 1378.39 | 1270.09
Dordi(27) | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 30 | 5.3 | 5.3
Upper Madi(25) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 25 | 8.4 | 8.4
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6 | [12 empty] | DAILY SYSTEM PEAK : 1877.35 MW
Upper Dordi (25) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 25 | 6.9 | 6.9 | [12 empty] | DAILY NATIONAL PEAK : 1877.35 MW
Solu Khola(23.5) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 23.5 | 7.8 | 7.8
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 22 | 12.5 | 12.5
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 20 | 6.5 | 6.5
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 21.9 | 22.5 | 21.9 | 21.1 | 22.1 | 22.4 | 21.5 | 21.5 | 20.1 | 18.7 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 21.5 | 21.5 | 22 | 23.3 | 21.1 | 19.5 | 18.9 | 17.1 | 17.1 | 15.7 | 15.3 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 240 | 23.3 | 15.3
Total IPP | 480.35 | 480.35 | 480.35 | 479.65 | 477.75 | 478.35 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.75 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 1042.4 | 480.35 | 477.75
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 270 | 270 | 250 | 15 | 15 | 50 | 76 | 55 | 40 | 75 | 87 | 100 | 140 | 120 | 150 | 130 | 130 | 110 | 80 | 40 | 0 | 456 | 270 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8.2 | 8.1 | 8.1 | 8.1 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 8.1 | 8.2 | 8.1 | 8.1 | 8.1 | 14.2 | 14.1 | 14.1 | 14.1 | 14.1 | 8.1 | 8.1 | 8.1 | 8.1 | 22.1 | 14.2 | 8
Total NEA SUBSIDIARIES | 35.1 | 35.1 | 35.1 | 35.1 | 35 | 35.2 | 35.1 | 35.1 | 95.1 | 96.2 | 306.2 | 306.2 | 286.2 | 51.2 | 51.2 | 86.2 | 112.2 | 90.1 | 75.2 | 110.1 | 122.1 | 135.1 | 181.2 | 161.1 | 191.1 | 171.1 | 171.1 | 145.1 | 115.1 | 75.1 | 35.1 | 538.1 | 306.2 | 35
KGA(144) | 0 | 0 | 0 | 0 | 0 | 30 | 91.5 | 97 | 144 | 111.8 | 92.1 | 93.8 | 93.8 | 60 | 60 | 60.7 | 60.7 | 71 | 98.2 | 81 | 31.2 | 30.1 | 61.4 | 140.6 | 136.4 | 94.6 | 81 | 81 | 81 | 30 | 0 | 144 | 144 | 0
Middle MRS(70) | 25 | 22.8 | 22.9 | 22.9 | 22.8 | 35 | 24.8 | 34.9 | 35.8 | 25 | 24.9 | 24.9 | 24.9 | 24 | 24 | 25 | 25 | 34.8 | 34.8 | 34.7 | 24.7 | 24.8 | 34.1 | 33.7 | 33.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 22 | 70 | 35.8 | 22
MRS(69) | 0 | 0 | 0 | 0 | 0 | 46 | 47 | 65.8 | 67 | 51 | 50 | 50 | 50 | 34 | 34 | 44.7 | 44.7 | 45.8 | 45.7 | 16.6 | 16.6 | 0 | 0 | 35.9 | 55 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 32 | 69 | 67 | 0
U Trisuli 3A(60) | 38 | 38 | 38 | 38 | 36 | 35 | 35.3 | 35.3 | 35.3 | 36.3 | 23.3 | 36 | 36 | 36 | 36 | 37.8 | 37.8 | 35.8 | 36 | 35 | 35 | 35 | 34.8 | 33.7 | 33.7 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 60 | 38 | 23.3
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10 | 13 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 28 | 28 | 10.2 | 0 | 0 | 0 | 0 | 10 | 22.7 | 22.7 | 23.6 | 15 | 15 | 10 | 10 | 0 | 30 | 28 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 1.7 | 3.2 | 5 | 13.1 | 15 | 18.7 | 18.7 | 16.3 | 11.5 | 6.9 | 1.9 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.7 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 10.2 | 10.2 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 14.1 | 10.7 | 10.2
MODI(14) | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 14 | 3.4 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5
Total ROR | 105.64 | 103.44 | 104.04 | 104.04 | 101.94 | 199.14 | 254.54 | 285.94 | 335.24 | 277.74 | 249.94 | 265.84 | 267.64 | 225.04 | 226.94 | 257.84 | 257.84 | 256.84 | 269.14 | 217.14 | 152.34 | 133.24 | 183.24 | 309.5 | 326.5 | 254.64 | 232.44 | 232.44 | 227.44 | 176.44 | 129.14 | 489.91 | 335.24 | 101.94
KL1(60) | 0.625: 14.2; 0.66667: 10.2; 0.70833: 0; 0.72917: 0; 0.75: 0; 0.77083: 0; 0.79167: 0; 0.8125: 0 | 60 | 14.2 | 0
KL2(32) | 0.3125: 5.2; 0.625: 4.9; 0.66667: 4.9; 0.70833: 0; 0.72917: 0; 0.75: 0; 0.77083: 0; 0.79167: 0; 0.8125: 0 | 32 | 5.2 | 0
KL3(14) | 0.3125: 1.9; 0.625: 1.8; 0.66667: 1.8; 0.70833: 0; 0.72917: 0; 0.75: 0; 0.77083: 0; 0.79167: 0; 0.8125: 0 | 14 | 1.9 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 20.9 | 0
TANAKPUR | 68.5 | 72.8 | 66.4 | 69 | 70 | 69.6 | 71 | 70 | 58 | 58 | 43 | 38.2 | 56 | 64 | 62.5 | 65.8 | 34.32 | 49.8 | 67.4 | 63.4 | 61.9 | 65.6 | 57.6 | 54.2 | 55 | 53.1 | 61.1 | 61.1 | 61.1 | 59 | 58 |  | 72.8 | 34.32
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 381 | 373.9 | 372.1 | 376.6 | 405 | 415 | 433 | 450 | 421 | 385 | 201 | 123 | 376 | 395 | 395 | 401 | 413 | 437.2 | 404.8 | 384.2 | 385 | 380.6 | 403 | 413.1 | 391 | 415 | 397 | 400 | 390 | 395 | 380 |  | 450 | 123
RAMNAGAR | 38 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 19 | 20 | 25 | 25 | 5 | 20 | 42 | 35 | 36 | 33 | 39 | 39 | 25 | 27.2 | 32 | 30.9 | 28.5 | 30 | 35 | 45 | 42 | 40 |  | 45 | 2
RAXAUL 132 | 18 | 16 | 0 | 0 |  |  | 20 | 19 | 20 | 20.4 | 23 | 10 | 11 | 0 | 0 | 103 | 111 | 112 | 113 | 119 | 86 | 51 | 49 | 80 | 79 | 82 | 82 | 106 | 100 | 98 | 96 |  | 119 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 50.7 | 54.6 | 51.6 | 53.5 | 48.3 | 45 | 48 | 49 | 72.7 | 65.4 | 59.1 | 55.4 | 53.3 | 55.6 | 67.8 | 71.1 | 67 | 66.8 | 73 | 74.1 | 70 | 60 | 70 | 75.9 | 76 | 67.5 | 75.4 | 71 | 60 | 58 | 58 |  | 76 | 45
Total IMPORT | 556.2 | 519.3 | 492.1 | 501.1 | 525.3 | 531.6 | 574 | 590 | 575.7 | 547.8 | 346.1 | 251.6 | 521.3 | 519.6 | 545.3 | 682.9 | 660.32 | 701.8 | 691.2 | 679.7 | 641.9 | 582.2 | 606.8 | 655.2 | 631.9 | 646.1 | 645.5 | 673.1 | 656.1 | 652 | 632 | 0 | 701.8 | 251.6
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1341.39 | 1388.79 | 1483.79 | 1399.49 | 1387.09 | 1301.39 | 1552.89 | 1273.59 | 1301.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1328.39 | 1449.09 | 1603.65 | 1627.35 | 1549.69 | 1526.89 | 1528.49 | 1476.49 | 1381.39 | 1274.09 | 2231.81 | 1627.35 | 1111.59
Interruption/Tripping | 0.29167: 250; 0.3125: 280; 0.33333: 280; 0.375: 280; 0.41667: 280; 0.45833: 280; 0.72917: 200; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 230; 0.83333: 200; 0.85417: 100; 0.875: 0; 0.91667: 0; 0.95833: 0 |  | 280 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1341.39 | 1388.79 | 1483.79 | 1649.49 | 1667.09 | 1581.39 | 1832.89 | 1553.59 | 1581.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1528.39 | 1699.09 | 1853.65 | 1877.35 | 1779.69 | 1726.89 | 1628.49 | 1476.49 | 1381.39 | 1274.09 | 1693.71 | 1877.35 | 1111.59
TOTAL NATIONAL LOAD (ACTUAL) | 1177.29 | 1138.19 | 1111.59 | 1119.89 | 1139.99 | 1244.29 | 1341.39 | 1388.79 | 1483.79 | 1649.49 | 1667.09 | 1581.39 | 1832.89 | 1553.59 | 1581.19 | 1504.69 | 1508.11 | 1526.49 | 1534.19 | 1501.69 | 1394.19 | 1528.39 | 1699.09 | 1853.65 | 1877.35 | 1779.69 | 1726.89 | 1627.49 | 1474.49 | 1378.39 | 1270.09 |  | 1877.35 | 1111.59
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 |  | 4 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 |  | 4 | 0
NET IMPORT | 556.2 | 519.3 | 492.1 | 501.1 | 525.3 | 531.6 | 574 | 590 | 575.7 | 547.8 | 346.1 | 251.6 | 521.3 | 519.6 | 545.3 | 682.9 | 660.32 | 701.8 | 691.2 | 679.7 | 641.9 | 582.2 | 606.8 | 655.2 | 631.9 | 646.1 | 645.5 | 672.1 | 654.1 | 649 | 628 |  | 701.8 | 251.6
HZ | 49.99 | 49.96 | 50.01 | 50.044 | 50.002 | 50.051 | 50.091 | 50.276 | 50.08 | 49.987 | 50.01 | 50.012 | 50.071 | 50.049 | 50.035 | 49.983 | 50.026 | 49.928 | 49.754 | 49.935 | 50 | 50.065 | 50.039 | 50.07 | 50.041 | 49.988 | 50.013 | 50.04 | 49.95 | 49.98 | 50.05 |  | 50.276 | 49.754
HTD 132KV | 130.5 | 129.6 | 129.8 | 128.3 | 126.7 | 127 | 127 | 125.8 | 126.4 | 129.3 | 126.5 | 126.5 | 127.8 | 126 | 127.7 | 125.6 | 123.8 | 125.2 | 127 | 127.3 | 128 | 127.5 | 125.6 | 126.8 | 127.3 | 127.5 | 128.3 | 128.3 | 128.3 | 129 | 129 |  | 130.5 | 123.8
SUI 132KV | 133.9 | 132.8 | 132.9 | 132.2 | 130.9 | 130.8 | 130.6 | 129.4 | 128.8 | 130.4 | 127.4 | 127.7 | 129.2 | 127.7 | 129.2 | 127.6 | 126.3 | 127.5 | 128.7 | 128.9 | 129.6 | 129 | 127 | 127.3 | 127.9 | 128.2 | 129.4 | 129.4 | 129.4 | 131.6 | 131.6 |  | 133.9 | 126.3
DUBI 132KV | 13.2 | 131.2 | 132 | 131.9 | 131.4 | 128.5 | 128.4 | 127.6 | 125.9 | 130.7 | 127.9 | 129 | 131.9 | 128 | 128.3 | 126.2 | 127.9 | 122.9 | 127.5 | 126.6 | 130.8 | 130.7 | 127.6 | 127 | 129.4 | 130.6 | 130 | 130 | 130 | 130 | 130 |  | 132 | 13.2
ANAMANI 132KV | 132.5 | 132.9 | 132.3 | 134 | 133.5 | 130.9 | 131.2 | 131.2 | 128.3 | 131.6 | 128.2 | 128.2 | 131.4 | 128.5 | 128.1 | 128.2 | 129.5 | 124.8 | 128.8 | 127.3 | 131 | 131.2 | 127.8 | 126.8 | 129.4 | 131.9 | 132.2 | 133 | 133 | 133 | 133 |  | 134 | 124.8
KG-A 132KV | 134.6 | 131.2 | 130.7 | 131.9 | 130.3 | 133.6 | 133.6 | 134.1 | 135.2 | 136.9 | 133.5 | 133.2 | 133.6 | 132.6 | 132.6 | 132.1 | 131.3 | 131.6 | 131.9 | 132 | 134.5 | 133.7 | 132 | 134.6 | 136.1 | 135.5 | 136.7 | 136.7 | 136.7 | 133.9 | 133.9 |  | 136.9 | 130.3
KOHALPUR 132KV | 133.5 | 131 | 133.8 | 133.4 | 134.6 | 130.5 | 128.7 | 134 | 130.8 | 129.3 | 129.6 | 131.9 | 134 | 134 | 127.5 | 131.7 | 135.7 | 131.2 | 130.6 | 131.9 | 134.6 | 129.1 | 133.7 | 131.2 | 130.8 | 133.9 | 136.3 | 133 | 133 | 133.6 | 133.6 |  | 136.3 | 127.5
SUI 66KV | 67.4 | 67.1 | 67.1 | 66.7 | 66.1 | 65.8 | 65.9 | 65.2 | 64.9 | 65.4 | 63.9 | 64.3 | 65.1 | 64.1 | 64.9 | 64.1 | 63.3 | 63.9 | 64.9 | 65.1 | 65.6 | 65.3 | 64.2 | 64.3 | 64.8 | 64.6 | 65.3 | 65.2 | 65.2 | 66.3 | 66.3 |  | 67.4 | 63.3
[33 empty] | 0 | 0
Kathmandu Load | 157.26 | 146.48 | 140.84 | 139.02 | 144.78 | 220.08 | 224.12 | 281.48 | 331.666 | 350.62 | 372.332 | 383.14 | 368.24 | 365.54 | 42 | 350.388 | 292.24 | 317.887 | 316.999 | 311.514 | 322.04 | 334.571 | 395.617 | 437.644 | 450.315 | 426.866 | 386.1 | 368.8 | 368.8 | 263.64 | 177.64 |  | 450.315 | 42
MRS-SYU | -0.3 | -7 | -7.9 | -5.4 | -9.5 | 18.1 | 17.4 | 22.2 | 33.4 | 30.7 | 25.6 | 30.2 | 29.1 | 29 | 34.7 | 24.9 | 25.3 | 26 | 30.4 | 17.5 | 11.4 | 11.4 | 26 | 37.1 | 40.7 | 31 | 30.2 | 28.6 | 28.6 | 13 | 0 | 75 | 40.7 | -9.5
NMRS-MATA | -3.3 | -12.2 | -13.5 | -9.2 | -15.3 | 19.1 | 18.3 | 22.2 | 37.5 | 39.9 | 32.9 | 39.6 | 39.7 | 40 | 41 | 27.1 | 29 | 28.5 | 35.8 | 20.2 | 16.6 | 16.3 | 35.9 | 49.7 | 53.6 | 39.7 | 39.4 | 38 | 38 | 11 | 4 | 240 | 53.6 | -15.3
KL2-MATA | -22.8 | -20.1 | -27.7 | -37 | -34 | -16.6 | -14.4 | 4.7 | 15.6 | 42 | 52 | 48 | 44 | 38 | 34 | 28.2 | 17 | 15.1 | 7.5 | 23 | 48.3 | 49 | 65 | 74 | 76 | 78 | 60 | 51 | 51 | 17 | 0 | 240 | 78 | -37
KL1-SYU | 2 | 0.6 | -1.5 | -2.5 | -2.3 | -5.4 | -4 | 2.6 | 15.1 | 21.3 | 23 | 22.7 | 21 | 21 | 22 | 27.9 | 6 | 2.3 | 12.6 | 18.2 | 15.4 | 19.9 | 25 | 28.2 | 29.2 | 29.2 | 20.3 | 15 | 15 | 7 | -2 | 60 | 29.2 | -5.4
KHIMTI-LAMOSANGHU | 90.72 | 94.24 | 100 | 101.68 | 116.44 | 116.44 | 118.08 | 141.04 | 141.126 | 126.28 | 160.392 | 150 | 140 | 135 | 140 | 132.348 | 105 | 140.447 | 129.759 | 137.274 | 140 | 149.131 | 155.477 | 155.644 | 157.815 | 163.326 | 150.56 | 150.56 | 150.56 | 130 | 90 | 120 | 163.326 | 90
LAMOSHANGU-BHAKTAPUR | 69.5 | 71.6 | 74.2 | 74.4 | 81.6 | 80.3 | 80.9 | 92.3 | 93.7 | 86 | 102.7 | 102 | 83.2 | 84 | 80 | 86.8 | 91 | 89.9 | 85 | 89.7 | 89.8 | 95.5 | 98.7 | 98.1 | 99 | 101.7 | 98.5 | 98.5 | 98.5 | 86 | 80
BALAJU-SYUCHATAR | 44.4 | 52.7 | 60 | 65.2 | 74.8 | 39.1 | 38.3 | 34.8 | 7.8 | -21.3 | -8.5 | -8.1 | -18.5 | -7 | 0.8 | 22.5 | 8 | 19.6 | 12.7 | 13.7 | 3.3 | 3.3 | -27.1 | -46.4 | -52.8 | -38.9 | -26 | -26 | -26 | 19 | 36
DHALKE-NAWALPUR I | 86.9 | 85.9 | 93.5 | 98.3 | 107.8 | 95.8 | 95.5 | 109 | 110 | 89 | 95.5 | 97 | 80.2 | 85 | 81 | 95.1 | 90 | 94.7 | 66.1 | 72 | 85.1 | 90.4 | 84.6 | 80.9 | 85.3 | 91.2 | 93.2 | 93.2 | 93.2 | 87 | 80 |  | 110 | 66.1
N. BHARATPUR-BARDGHAT I | 13.8 | 21.6 | 21.6 | 18.5 | 21.3 | 5.9 | 6.2 | 9 | -10.5 | -4.7 | 0 | -4.7 | -6 | -4 | -11 | -4.6 | -5 | 0 | -6.4 | -1.3 | 6.7 | 3.7 | -2.7 | -17.9 | -12.7 | -6.8 | -5 | -5 | -5 | 12 | 17 |  | 21.6 | -17.9
DAMAK-DUHABI | -6.7 | -4.9 | -4.9 | -4.5 | -5.3 | -15.5 | -15.8 | -23.3 | -33.3 | -37.5 | -42.6 | -41.9 | -32 | -26 | -22 | -14.1 | -18 | -17.4 | -16.8 | -28.5 | -33.1 | -37.6 | -52.6 | -53.2 | -49 | -43.1 | -31.3 | -31.3 | -31.3 | -15 | -11 |  | -4.5 | -53.2
HETAUDA-KAMANE | 2.8 | -6.3 | 2.4 |  | 4.8 | -3.3 | -3.1 | -12.8 | -8.5 | -29.9 | -36.3 | -33.9 | -30 | -27 | -24 | -32.6 | -23 | -20.5 | -6.8 | -21.7 | -47.8 | -45.5 | -46.9 | -43.6 | -45.4 | -52.8 | -45.3 | -45.3 | -45.3 | -29 | -26 |  | 4.8 | -52.8
MIRCHAIYA LAHAN 2 | 81.3 | 78.2 | 71.9 |  | 71.9 | 81.1 | 84.3 | 87.3 | 96.1 | 93.7 | 81.7 | 84.5 | 70 | 86 | 102 | 101.1 | 102 | 110.9 | 111 | 112.1 | 100.8 | 100 | 117.1 | 123.8 | 115.7 | 106.2 | 108 | 108 | 108 | 103 | 93 |  | 123.8 | 70
Water Level
UTK | 1984.3 | 1984.5 | 1984.7 | 1984.95 | 1985.15 | 1985.35 |  | 1985.52 |  | 1985.62 |  | 1985.15 | 1984.62 | 1984.77 | 1984.95 | 1985.05 | 1985.05 | 1985.03 | 1885 | 1984.98 | 1984.9 |  | 1984.82 |  | 1984.68 |  | 1984.52 |  | 1954.49 | 1984.5
KGA | 521.09 | 521.45 | 521.75 | 522.08 | 522.36 | 522.63 |  | 522.57 |  | 522.16 |  | 521.9 | 521.68 | 521.62 | 521.54 | 521.48 | 521.42 | 521.32 | 521.15 | 520.93 | 520.8 |  | 520.92 |  | 520.48 |  | 520.12 |  | 519.94 | 519.8
MMRS | 622.07 | 622.17 | 622.29 | 622.43 | 622.5 | 622.57 |  | 622.56 |  | 622.51 |  | 622.7 | 622.75 | 622.7 | 622.82 | 622.83 | 622.86 | 622.8 | 622.68 | 622.55 | 622.51 |  | 622.43 |  | 622.29 |  | 622.19 |  | 622.15 | 622.1 | 622.1
MRS | 335.19 | 335.51 | 335.89 |  | 336.4 | 336.52 |  | 336.36 |  | 336.06 |  | 335.8 | 335.61 | 335.54 | 335.49 | 335.47 | 335.43 | 335.33 | 335.17 | 335.01 | 335.14 |  | 335.37 |  | 335.29 | 335.22 | 335.22 |  | 335.23 | 335.24 | 335.23
CHM | 885.8 | 886.3 | 886.8 | 887.2 | 887.6 | 887.6 |  |  |  | 887.3 |  | 88.7.1 | 886.8 | 886.6 | 886.3 | 885.7 | 884.6 | 884.5 | 884.8 | 885.3 | 885.9 |  | 886.3 |  | 885.7 |  | 884.4 |  | 884.2 | 884.1
KL 1 | 0.58333: 1519.42; 0.66667: 1519.42; 0.70833: 1519.41; 0.79167: 1519.42
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1832.89; 0.041667: 9:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/13)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 14
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/14 |  |  | 2080/10/14 |  |  | Monday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 576 | 596 | 601 | 594 | 672.4 | 673 | 669 | 681.6 | 611.6 | 360.7 | 243.2 | 449 | 552 | 616 | 675.5 | 702.8 | 636.8 | 719.2 | 740.9 | 587.5 | 607.6 | 627.1 | 454.4 | 326 | 326.4 | 457.1 | 601.4 | 674.3 | 697.7 | 632.9 | 611
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1714MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1186 | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1303.09 | 1289.09 | 1498.09 | 1607.29 | 1714.29 | 1649.29 | 1554.39 | 1574.59 | 1530.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1486.59 | 1602.49 | 1688.09 | 1844.99 | 1826.59 | 1772.59 | 1620.19 | 1579.89 | 1592.99 | 1393.29 | 1280.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [14 empty] | DAILY SYSTEM PEAK : 1826.59 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [9 empty] | DAILY NATIONAL PEAK : 1826.59 MW
Solu Khola Dudhkoshi(86) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 86 | 30.2 | 27
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 14
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/14)
Likhu-IV(52.4) | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 52.4 | 15.2 | 15.2
Upper Marsyangdi "A"(50) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 50 | 28.6 | 28.6 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 45 | 15.8 | 15.8 |  | IPP | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 478.55 | 478.55 | 478.55 | 478.55
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 95.1 | 339.9 | 85.9 | 70.9 | 60.9 | 135.9 | 115.8 | 115.8 | 75.8 | 75.8 | 65.8 | 65.8 | 421.1 | 231.1 | 111.2 | 75.2 | 65.2
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7.5 |  | NEA ROR PROR | 97.14 | 97.14 | 97.14 | 97.14 | 107.14 | 107.14 | 107.14 | 272.74 | 308.34 | 261.64 | 223.84 | 225.74 | 258.44 | 260.44 | 238.24 | 236.54 | 228.44 | 205.44 | 267.34 | 351.64 | 253.44 | 208.94 | 141.84 | 104.14
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 611 | 576 | 596 | 601 | 594 | 672.4 | 669 | 611.6 | 243.2 | 449 | 552 | 616 | 675.5 | 702.8 | 636.8 | 719.2 | 740.9 | 587.5 | 627.1 | 326 | 457.1 | 674.3 | 697.7 | 632.9
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 280 | 280 | 250 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 250 | 250 | 200 | 120 | 0 | 0
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8 |  | System_Load | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1289.09 | 1607.29 | 1649.29 | 1554.39 | 1574.59 | 1530.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1486.59 | 1688.09 | 1826.59 | 1620.19 | 1592.99 | 1393.29 | 1280.79
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 24.2 | 6.2 | 6.2 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 28 | 7.3 | 7.3 |  | National_Load | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1289.09 | 1607.29 | 1649.29 | 1554.39 | 1574.59 | 1530.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1486.59 | 1688.09 | 1826.59 | 1620.19 | 1592.99 | 1393.29 | 1280.79
Dordi(27) | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 30 | 5.3 | 5.3
Upper Madi(25) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 25 | 8.4 | 8.4
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 25 | 6.9 | 6.9
Solu Khola(23.5) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 23.5 | 7.8 | 7.8
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 22 | 12.5 | 12.5
Lower Modi (20) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 4 | 4 | 4 | 4 | 4 | 20 | 6.5 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 18.2 | 18.2 | 18.2 | 21.1 | 21.6 | 20.9 | 20.9 | 20.9 | 21 | 19.4 | 19.4 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 240 | 22.8 | 16.2
Total IPP | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 477.85 | 478.55 | 478.55 | 478.55 | 478.55 | 478.55 | 1042.4 | 478.55 | 477.85
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 60 | 304 | 304 | 50 | 35 | 25 | 100 | 80 | 80 | 40 | 40 | 30 | 30 | 30 | 270 | 380 | 360 | 190 | 50 | 70 | 40 | 30 | 456 | 380 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 14.1 | 14.1 | 14.1 | 14.1 | 14 | 14.2 | 8.2 | 8.2 | 22.1 | 14.2 | 8.1
Total NEA SUBSIDIARIES | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1 | 115.1 | 95.1 | 339.1 | 339.9 | 85.9 | 70.9 | 60.9 | 135.9 | 115.8 | 115.8 | 75.8 | 75.8 | 65.8 | 65.8 | 65.8 | 311.1 | 421.1 | 401.1 | 231.1 | 91 | 111.2 | 75.2 | 65.2 | 538.1 | 421.1 | 35.1
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 61.1 | 98.2 | 142 | 113.2 | 62 | 61 | 61 | 73.4 | 73.6 | 61.7 | 61.7 | 61.3 | 61.3 | 61.3 | 93.2 | 141.4 | 141.4 | 112.1 | 73.3 | 45.3 | 45.3 | 0 | 0 | 144 | 142 | 0
Middle MRS(70) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 35 | 27 | 35 | 34.8 | 34.8 | 25 | 25 | 25.6 | 32.2 | 24.9 | 34.8 | 34.8 | 27.6 | 24.8 | 25.1 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 22.9 | 70 | 35 | 22
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3 | 62.1 | 67.2 | 62.1 | 62.1 | 32 | 32 | 33.3 | 33.4 | 47.7 | 47.2 | 47.2 | 34.1 | 33.5 | 67.8 | 68 | 68 | 64.2 | 54.3 | 37.8 | 37.8 | 16 | 0 | 69 | 68 | 0
U Trisuli 3A(60) | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 37.3 | 37.3 | 37.3 | 37.3 | 38 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.6 | 36.3 | 36.3 | 36.3 | 38.3 | 38.3 | 60 | 38.6 | 32.2
CHM(30) | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 14 | 14 | 10 | 10 | 27 | 23.2 | 10.2 | 0 | 0 | 0 | 0 | 0 | 26.2 | 26.2 | 25.6 | 11.8 | 11.8 | 11.8 | 9.8 | 0 | 30 | 27 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 2.3 | 4 | 8.5 | 15.6 | 17.5 | 18.2 | 16.8 | 12.5 | 11.6 | 3.9 | 1.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.2 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 14.1 | 10.7 | 10.7
MODI(14) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 14 | 3.2 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 97.14 | 97.14 | 97.14 | 97.14 | 107.14 | 107.14 | 117.14 | 107.14 | 223.54 | 272.74 | 336.64 | 308.34 | 261.64 | 223.84 | 225.74 | 258.44 | 260.44 | 238.24 | 236.54 | 228.44 | 205.44 | 201.24 | 267.34 | 351.64 | 351.64 | 318.24 | 253.44 | 208.94 | 208.94 | 141.84 | 104.14 | 489.91 | 351.64 | 97.14
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 45 | 70 | 70 | 78 | 67.2 | 69 | 75 | 71 | 50.6 | 64.3 | 61.6 | 56.2 | 43 | 55 | 55 | 66 | 69.8 | 67.1 | 56.8 | 66.2 | 63.6 | 61.6 | 66.8 | 60 | 68.2 | 62 | 58 | 59 | 56.9 | 56.5 | 59.6 |  | 78 | 43
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 390 | 400 | 400 | 399 | 413.2 | 436.4 | 445 | 442 | 438 | 407.1 | 160.1 | 79 | 297 | 392 | 401 | 391 | 404 | 369.2 | 453.5 | 466.8 | 395.6 | 421.8 | 437.3 | 271.4 | 132.6 | 131.8 | 257.8 | 399 | 423 | 413.4 | 380.5 |  | 466.8 | 79
RAMNAGAR | 6 | 6 | 6 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 24 | 42 | 41 | 26 | 21.5 | 26.9 | 6.7 | 9.5 | 8.4 | 8.4 | 6.7 | 6.7 | 10.3 | 13 | 20 | 38.8 | 38.9 |  | 42 | 3
RAXAUL 132 | 120 | 100 | 120 | 118 | 110.6 | 112 | 105 | 108 | 114 | 66.8 | 66 | 36 | 36 | 28 | 60 | 102 | 108 | 102.2 | 110.6 | 103 | 60 | 54.4 | 51.2 | 51.2 | 50 | 57.4 | 70 | 69 | 101 | 119 | 84 |  | 120 | 28
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 50 | 0 | 0 | 0 | 0 | 52 | 45 | 45 | 76 | 70.4 | 70 | 67 | 68 | 72 | 76 | 74.5 | 80 | 72.3 | 76.8 | 78 | 61.6 | 60.3 | 63.4 | 63.4 | 68.5 | 68.5 | 61 | 61.4 | 73.4 | 70 | 69.9 |  | 80 | 0
Total IMPORT | 611 | 576 | 596 | 601 | 594 | 672.4 | 673 | 669 | 681.6 | 611.6 | 360.7 | 243.2 | 449 | 552 | 616 | 675.5 | 702.8 | 636.8 | 719.2 | 740.9 | 587.5 | 607.6 | 627.1 | 454.4 | 326 | 326.4 | 457.1 | 601.4 | 674.3 | 697.7 | 632.9 | 0 | 740.9 | 243.2
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1303.09 | 1289.09 | 1498.09 | 1457.29 | 1514.29 | 1369.29 | 1274.39 | 1324.59 | 1380.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1336.59 | 1352.49 | 1438.09 | 1594.99 | 1576.59 | 1523.59 | 1420.19 | 1379.89 | 1472.99 | 1393.29 | 1280.79 | 2231.81 | 1594.99 | 1186.09
Interruption/Tripping | 0.29167: 150; 0.3125: 200; 0.33333: 280; 0.375: 280; 0.41667: 250; 0.45833: 150; 0.70833: 150; 0.72917: 250; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 200; 0.85417: 200; 0.875: 120 |  | 280 | 120
TOTAL SYSTEM LOAD (EXPECTED) | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1303.09 | 1289.09 | 1498.09 | 1607.29 | 1714.29 | 1649.29 | 1554.39 | 1574.59 | 1530.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1486.59 | 1602.49 | 1688.09 | 1844.99 | 1826.59 | 1773.59 | 1620.19 | 1579.89 | 1592.99 | 1393.29 | 1280.79 | 1693.71 | 1844.99 | 1186.09
TOTAL NATIONAL LOAD (ACTUAL) | 1221.09 | 1186.09 | 1206.09 | 1211.09 | 1214.09 | 1292.49 | 1303.09 | 1289.09 | 1498.09 | 1607.29 | 1714.29 | 1649.29 | 1554.39 | 1574.59 | 1530.49 | 1547.69 | 1556.89 | 1468.69 | 1509.39 | 1522.99 | 1486.59 | 1602.49 | 1688.09 | 1844.99 | 1826.59 | 1772.59 | 1620.19 | 1579.89 | 1592.99 | 1393.29 | 1280.79 |  | 1844.99 | 1186.09
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
NET IMPORT | 611 | 576 | 596 | 601 | 594 | 672.4 | 673 | 669 | 681.6 | 611.6 | 360.7 | 243.2 | 449 | 552 | 616 | 675.5 | 702.8 | 636.8 | 719.2 | 740.9 | 587.5 | 607.6 | 627.1 | 454.4 | 326 | 325.4 | 457.1 | 601.4 | 674.3 | 697.7 | 632.9 |  | 740.9 | 243.2
HZ | 50.02 | 50.02 | 50.03 | 50.043 | 50.03 | 50 | 50.04 | 50.059 | 50.034 | 49.974 | 50.018 | 50.043 | 49.952 | 49.945 | 50.08 | 50.037 | 49.948 | 50.13 | 49.92 | 50.06 | 50.02 | 50.14 | 50.07 | 50.06 | 49.99 | 50.07 | 50.177 | 50.022 | 50.066 | 50.105 | 49.987 |  | 50.177 | 49.92
HTD 132KV | 129.7 | 129.4 | 129.7 | 129.4 | 128.66 | 129 | 128.4 | 128.4 | 125.9 | 127.1 | 126.4 | 125.8 | 126.1 | 126.1 | 126.1 | 127.3 | 125.9 | 125.2 | 124.1 | 124.2 | 129.7 | 128 | 127.8 | 125.9 | 126.1 | 126.1 | 129.1 | 128.6 | 126.8 | 128.8 | 129.1 |  | 129.7 | 124.1
SUI 132KV | 132.7 | 132 | 132.6 | 132.5 | 131.8 | 132.2 | 131.5 | 131.2 | 128.2 | 128 | 127.2 | 126.6 | 127.6 | 127.6 | 127.9 | 129.2 | 128.2 | 127.8 | 127 | 125.3 | 131 | 129.5 | 129.2 | 126.6 | 127 | 127 | 130.4 | 130.1 | 129.2 | 126.3 | 132.1 |  | 132.7 | 125.3
DUBI 132KV | 131 | 131 | 131 | 128.9 | 126.2 | 128.1 | 126.4 | 127.5 | 126.8 | 127.6 | 125.2 | 127.45 | 128.5 | 129.2 | 127.5 | 127 | 127.2 | 125.3 | 123.8 | 126.6 | 131.9 | 127.6 | 128.5 | 130.5 | 131.1 | 131.1 | 130.2 | 130.4 | 126.6 | 127.7 | 128.4 |  | 131.9 | 123.8
ANAMANI 132KV | 133 | 133.9 | 132 | 130 | 128.1 | 130.1 | 128.2 | 130.98 | 128.7 | 129 | 125.4 | 127.5 | 128.7 | 129.7 | 129.4 | 128.7 | 129 | 126.6 | 125.3 | 126.6 | 132 | 128.4 | 127.8 | 129.2 | 131.4 | 131.4 | 132.2 | 132.8 | 130 | 131.2 | 130.2 |  | 133.9 | 125.3
KG-A 132KV | 130.6 | 130.4 | 131.4 | 131.4 | 129.8 | 132.9 | 134.7 | 134 | 132.4 | 135.9 | 133.5 | 133.3 | 132.1 | 133.4 | 133.5 | 137.8 | 133.3 | 132.2 | 131.3 | 130.5 | 136.7 | 135 | 134.5 | 132.9 | 132.9 | 132.9 | 136.2 | 135 | 132 | 130.9 | 132.3 |  | 137.8 | 129.8
KOHALPUR 132KV | 133 | 132.8 | 125 | 135 | 131.9 | 129.5 | 126.2 | 136 | 139.3 | 126.7 | 130.1 | 129.1 | 132.7 | 130.5 | 133.9 | 128.6 | 130 | 130.9 | 132.7 | 126.9 | 130.98 | 133.4 | 133.4 | 131.2 | 128.9 | 128.9 | 132 | 131 | 133.5 | 131.8 | 133 |  | 139.3 | 125
SUI 66KV | 67.2 | 66.6 | 66.6 | 67 | 66.6 | 66.9 | 66.8 | 66 | 64.3 | 64.6 | 64.2 | 63.8 | 64.4 | 64.3 | 64.3 | 65.2 | 64.9 | 64.7 | 64.5 | 64.2 | 66.1 | 65 | 64.6 | 63.4 | 63.6 | 63.6 | 65.5 | 65.1 | 64.9 | 65.8 | 66.3 |  | 67.2 | 63.4
[33 empty] | 0 | 0
Kathmandu Load | 159.64 | 114.24 | 112.64 | 137.54 | 134.24 | 156.02 | 193.4 | 233.54 | 275.24 | 366.16 | 396.78 | 399.908 | 363.94 | 356.14 | 42 | 333.284 | 334.208 | 306.04 | 307.08 | 312.26 | 312.56 | 329.24 | 368.52 | 429.28 | 433.98 | 416.88 | 388.089 | 363.052 | 321.662 | 253.399 | 187.03 |  | 433.98 | 42
MRS-SYU | -18 | -18 | -25 | -15.7 | -19.3 | -10.3 | 1.3 | 9.3 | 13.4 | 29.4 | 45 | 34.5 | 22.5 | 25.1 | 29.7 | 26.3 | 25.1 | 18.9 | 17.7 | 18.9 | 22.9 | 20.3 | 37.1 | 40.2 | 42.74 | 41.5 | 31.9 | 23.7 | 21 | 8.8 | -3.6 | 75 | 45 | -25
NMRS-MATA | 4 | -28 | -17 | -23 | -29.3 | -18 | -0.9 | 7 | 10.4 | 37.3 | 59.2 | 46.4 | 32.2 | 34.7 | 34 | 30 | 27.6 | 20 | 18.4 | 18.4 | 31.5 | 27.9 | 48.2 | 52.9 | 56.4 | 55.1 | 41.8 | 32.3 | 23.5 | 7.1 | -9.3 | 240 | 59.2 | -29.3
KL2-MATA | 0 | -5.4 | -7 | -11 | -9 | -7 | 0 | 8 | 20 | 52 | 45 | 44.6 | 45 | 44 | 33 | 26.4 | 24 | 18 | 20 | 24 | 33 | 40 | 44 | 58 | 57 | 50 | 55.4 | 51 | 31.2 | 12 | -3.9 | 240 | 58 | -11
KL1-SYU | -2 | -10 | -9 | -12 | -9 | -10 | 0 | 2 | 5 | 22 | 23 | 21.9 | 20 | 21 | 14 | 10.4 | 7.6 | 4.1 | 1.4 | 6.2 | 18.3 | 22.5 | 25.4 | 29.8 | 30.1 | 29.6 | 27.8 | 26.7 | 11.6 | 4 | 0.2 | 60 | 30.1 | -12
KHIMTI-LAMOSANGHU | 90 | 90 | 85 | 113.6 | 115.2 | 115.68 | 107.36 | 121.6 | 140.8 | 139.52 | 136.64 | 157.768 | 145 | 125 | 110 | 130.544 | 141.368 | 140.8 | 146.24 | 149.12 | 113.92 | 126.4 | 122.08 | 156.64 | 156 | 148.64 | 141.449 | 139.612 | 144.622 | 129.759 | 111.89 | 120 | 157.768 | 85
LAMOSHANGU-BHAKTAPUR | 80 | 83 | 81 | 81 | 82 | 82 | 78 | 85 | 94 | 94 | 92.3 | 100.4 | 90 | 88.3 | 85.8 | 87.7 | 89 | 92.9 | 96.1 | 97.1 | 77.8 | 85.6 | 82.4 | 100.9 | 100.2 | 96.8 | 91.5 | 90.4 | 83.6 | 86.2 | 79.2
BALAJU-SYUCHATAR | 36 | 65 | 65 | 66 | 72.5 | 58 | 45.3 | 35 | 30 | -32.3 | -47 | 26.4 | -11 | -14 | -1.5 | 6.7 | 15.7 | 26.5 | 27.3 | 23.7 | -12.8 | -6.2 | -28.9 | -33.8 | -34.2 | -31.6 | -25.5 | -15.3 | 8.7 | 36.6 | 54.7
DHALKE-NAWALPUR I | 80 | 95 | 89 | 87 | 87 | 86 | 79 | 90 | 95 | 92 | 69 | 83.2 | 89 | 83 | 81 | 86.7 | 85 | 90.4 | 95.5 | 98.5 | 72.2 | 83.2 | 77.6 | 85.1 | 78.4 | 74.9 | 77 | 88.9 | 89.2 | 82 | 80.8 |  | 98.5 | 69
N. BHARATPUR-BARDGHAT I | 17 | 40 | 37 | 35.1 | 40 | 29 | 20 | 20 | 12.1 | 3.4 | -13 | -3.4 | 1.8 | 0 | -4.7 | -9.5 | -5.3 | 2.1 | 4.7 | 2.2 | -1 | -2.2 | -8.1 | -15 | -17.3 | -14.3 | -3.1 | 0 | 4.4 | 11.9 | 17 |  | 40 | -17.3
DAMAK-DUHABI | -11 | -6.5 | -6.5 | -6.3 | -6.1 | -11 | -16.2 | -24 | -33 | -41.4 | -46 | -45.6 | -33 | -26.5 | -15 | -16 | -16.2 | -21.3 | -22 | -29.5 | -34.3 | -42.5 | -53.2 | -61.2 | -52.2 | -42 | -35.5 | -30.6 | -23 | -20.9 | -11.5 |  | -6.1 | -61.2
HETAUDA-KAMANE | -26 | -38 | -31 | -31.6 | 32.3 | -25 | -21.5 | -26.3 | -29.4 | -39 | -20 | -27.5 | -35 | -33.4 | -27 | -26.2 | 28 | -26.6 | -32.2 | -30.4 | -26.7 | -33.1 | -27.2 | -34.2 | -31.3 | -27.41 | -29.7 | -38.6 | -36.4 | -23 | -21.1 |  | 32.3 | -39
MIRCHAIYA LAHAN 2 | 93 | 84 | 82 | 88 | 93.1 | 97 | 96 | 98.3 | 111.2 | 100 | 110 | 100 | 97 | 90.3 | 96 | 120 | 111.6 | 116 | 120.9 | 115.9 | 96.6 | 97.2 | 108.8 | 117.7 | 108.1 | 103.2 | 99 | 94.3 | 108.1 | 102.1 | 100.6 |  | 120.9 | 82
Water Level
UTK | 1984.9 | 1985.1 | 1985.32 | 1985.5 | 1985.7 | 1985.9 |  | 1986.1 |  | 1986.12 |  | 1985.7 | 1984.85 | 1984.75 | 1984.85 | 1984.8 | 1984.75 | 1984.7 | 1984.59 | 1984.63 | 1984.63 |  | 1984.77 |  | 1984.32 |  | 1983.3 |  | 1983.38 | 1983.4 | 1983.48
KGA | 520.48 | 520.85 | 521.14 | 521.48 | 521.78 | 522.08 |  | 522.23 |  | 522.12 |  | 521.71 | 521.44 | 521.34 | 521.28 | 521.19 | 521.04 | 520.98 | 520.9 | 520.82 | 520.72 |  | 520.58 |  | 519.96 |  | 519.4 |  | 519.39 | 519.47 | 519.86
MMRS | 622.15 | 622.21 | 622.32 | 622.39 | 622.42 | 622.58 |  | 622.58 |  | 622.46 |  | 622.4 | 622.49 | 622.55 | 622.6 | 622.66 | 622.72 | 622.69 | 622.7 | 622.59 | 622.59 |  | 622.55 |  | 622.45 |  | 622.31 |  | 622.19 | 622.1 | 622.1
MRS | 335.38 | 335.7 | 336 | 336.32 | 336.55 | 336.79 |  | 336.89 |  | 336.73 |  | 336.4 | 336.19 | 336.15 | 336.12 | 336.1 | 336.11 | 336.12 | 335.97 | 335.82 | 335.66 |  | 335.57 |  | 335.15 |  | 334.85 |  | 334.54 | 334.45 | 334.7
CHM | 885.1 | 885.5 | 886.2 | 886.7 | 886.7 | 886.9 |  | 886.7 |  | 886.6 |  | 886.4 | 886.1 | 885.9 | 885.8 | 885.3 | 884.1 | 882.9 | 883 | 883.8 | 884.4 |  | 885 |  | 884.2 |  | 883 |  | 882.6 | 882.4 | 882.8
KL 1 | 0.25: 1519.44; 0.83333: 1519.46
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1714.29; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/14)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 15
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/15 |  |  | 2080/10/15 |  |  | Tuesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 623.9 | 639.3 | 624.4 | 626.3 | 649.8 | 663.1 | 668.6 | 677.5 | 627.1 | 626.4 | 558.9 | 556.9 | 558.3 | 590.9 | 676.6 | 680 | 727.9 | 691.3 | 684.7 | 604.3 | 594.9 | 601.4 | 606.4 | 597.7 | 620.3 | 580.8 | 628.6 | 674.2 | 738 | 705 | 620.5
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1737MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1215 | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1289.79 | 1433.39 | 1550.89 | 1639.29 | 1736.69 | 1669.69 | 1607.29 | 1591.59 | 1494.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1550.19 | 1580.19 | 1656.99 | 1819.69 | 1851.29 | 1732.59 | 1693.09 | 1681.29 | 1440.89 | 1474.69 | 1307.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1852.29 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1851.29 MW
Solu Khola Dudhkoshi(86) | 28 | 25.4 | 27.6 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 28.4 | 27.2 | 27.2 | 25 | 27.8 | 30.5 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 86 | 30.5 | 25
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 15
Super Dordi (54) | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10.1 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/15)
Likhu-IV(52.4) | 15.2 | 15.2 | 15.2 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 52.4 | 15.3 | 15
Upper Marsyangdi "A"(50) | 26 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 50 | 29.4 | 26 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 45 | 16.4 | 15.3 |  | IPP | 474.15 | 472.55 | 476.75 | 477.65 | 477.65 | 477.65 | 477.65 | 477.65 | 471.65 | 471.65 | 469.45 | 472.25 | 474.95 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.3 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 150.7 | 122.2 | 147.3 | 107.3 | 87.2 | 67.2 | 137.2 | 135.7 | 125.7 | 184.7 | 184.7 | 74.7 | 131.2 | 201.2 | 121.1 | 121.1 | 91.1 | 41.1
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 42 | 7.5 | 6.5 |  | NEA ROR PROR | 103.54 | 103.54 | 77.74 | 77.74 | 102.34 | 113.14 | 136.44 | 262.34 | 291.84 | 271.44 | 276.64 | 264.04 | 255.44 | 242.24 | 233.54 | 217.58 | 241.48 | 206.34 | 209.54 | 338.54 | 276.34 | 180.74 | 180.74 | 96.74
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 620.5 | 623.9 | 639.3 | 624.4 | 626.3 | 649.8 | 668.6 | 627.1 | 558.9 | 556.9 | 558.3 | 590.9 | 676.6 | 680 | 727.9 | 691.3 | 684.7 | 604.3 | 601.4 | 597.7 | 580.8 | 674.2 | 738 | 705
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 200 | 200 | 200 | 100 | 0 | 0 | 0 | 0 | 0 | 200 | 250 | 250 | 250 | 0 | 0 | 0
Nyadi(30) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 30 | 7.9 | 7.2 |  | System_Load | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1433.39 | 1639.29 | 1669.69 | 1607.29 | 1591.59 | 1494.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1550.19 | 1656.99 | 1852.29 | 1693.09 | 1440.89 | 1474.69 | 1307.69
Likhu Khola A(29.04) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 6.2 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 28 | 7.5 | 7.3 |  | National_Load | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1433.39 | 1639.29 | 1669.69 | 1607.29 | 1591.59 | 1494.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1550.19 | 1656.99 | 1851.29 | 1693.09 | 1440.89 | 1474.69 | 1307.69
Dordi(27) | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 30 | 6.4 | 5.3
Upper Madi(25) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 25 | 8.4 | 6.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 25 | 6.9 | 6.9
Solu Khola(23.5) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 23.5 | 7.8 | 7.1
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 22 | 12.5 | 6.2
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 16.2 | 16.2 | 19.9 | 19.9 | 19.9 | 20.8 | 20.2 | 19.7 | 20.7 | 20.3 | 19.6 | 19.7 | 20.2 | 21.4 | 19.3 | 18.6 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 240 | 21.4 | 14
Total IPP | 474.15 | 472.55 | 476.75 | 477.65 | 477.65 | 477.65 | 477.65 | 477.65 | 477.65 | 477.65 | 477.65 | 471.65 | 471.65 | 469.45 | 472.25 | 474.95 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 464.85 | 1042.4 | 477.65 | 464.85
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 130 | 85 | 130 | 110 | 70 | 50 | 30 | 100 | 100 | 90 | 150 | 150 | 40 | 30 | 90 | 170 | 160 | 80 | 80 | 80 | 80 | 50 | 0 | 456 | 170 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.3 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 10.2 | 10.2 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 8.7 | 8.7 | 7.7 | 7.7 | 7.7 | 7.7 | 14.2 | 14.2 | 14.2 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 22.1 | 14.2 | 7.7
Total NEA SUBSIDIARIES | 35.3 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 35.7 | 150.7 | 165.7 | 122.2 | 167.2 | 147.3 | 107.3 | 87.2 | 67.2 | 137.2 | 135.7 | 125.7 | 184.7 | 184.7 | 74.7 | 64.7 | 131.2 | 211.2 | 201.2 | 121.1 | 121.1 | 121.1 | 121.1 | 91.1 | 41.1 | 538.1 | 211.2 | 35.3
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.2 | 91.7 | 91.4 | 110 | 92 | 91 | 91.8 | 81 | 70.7 | 71.5 | 60.9 | 75.4 | 61.9 | 61.9 | 61.9 | 96.6 | 132.6 | 85.4 | 85.4 | 46 | 31 | 31 | 0 | 144 | 132.6 | 0
Middle MRS(70) | 22.8 | 22.8 | 0 | 0 | 24.6 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | 32.74 | 32.74 | 25.1 | 25.1 | 25.1 | 33.8 | 33.8 | 25.7 | 25.7 | 21 | 22 | 22 | 22 | 70 | 35.4 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.3 | 42.3 | 45.1 | 45.5 | 46.5 | 46.3 | 46.3 | 32.9 | 33 | 32.7 | 32.7 | 32.8 | 45.9 | 32.6 | 32.6 | 32.6 | 58.1 | 68.5 | 69 | 69 | 65 | 43 | 43 | 0 | 69 | 69 | 0
U Trisuli 3A(60) | 38.3 | 38.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.5 | 36.3 | 36.3 | 36.3 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 38.3 | 35
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 10.5 | 10.9 | 15 | 10 | 10 | 10 | 10 | 15.1 | 9.5 | 10 | 10 | 10 | 10 | 14.4 | 23.2 | 28.1 | 21.5 | 21.5 | 10 | 10 | 10 | 0 | 30 | 28.1 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 2 | 5.6 | 8.4 | 14.6 | 14.6 | 16.7 | 10.8 | 6.9 | 5.6 | 1.9 | 1.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16.7 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4
DEVI(14.1) | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 14.1 | 10.1 | 7.5
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 14 | 3.3 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54
Total ROR | 103.54 | 103.54 | 77.74 | 77.74 | 102.34 | 113.14 | 113.34 | 136.44 | 230.04 | 262.34 | 265.44 | 291.84 | 271.44 | 276.64 | 264.04 | 255.44 | 242.24 | 233.54 | 217.58 | 241.48 | 206.34 | 205.74 | 209.54 | 287.24 | 338.54 | 276.34 | 276.34 | 216.74 | 180.74 | 180.74 | 96.74 | 489.91 | 338.54 | 77.74
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 68.5 | 65.9 | 63.6 | 56.4 | 58.4 | 58 | 62 | 63.7 | 64.6 | 65.6 | 67.3 | 62.3 | 58 | 57 | 56.9 | 69.8 | 68 | 62.3 | 67.3 | 69.5 | 61.7 | 64.8 | 67.3 | 67.8 | 64.9 | 59.4 | 59 | 62 | 70 | 70 | 64 |  | 70 | 56.4
KATAIYA | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0; 0.375: 0 |  | 0 | 0
MUJAFFARPUR | 415.7 | 396 | 412.3 | 401 | 386.5 | 405 | 413 | 407.6 | 413.6 | 394.7 | 400 | 398 | 395.8 | 392.3 | 389 | 389.2 | 400 | 442.1 | 399.6 | 403.1 | 382.7 | 393.9 | 390 | 381.1 | 372.8 | 392.3 | 382 | 385 | 407 | 435 | 411 |  | 442.1 | 372.8
RAMNAGAR | 4 | 4 | 4 | 4 | 4 | 40 | 41 | 45 | 44 | 36 | 34 | 35 | 35 | 35 | 45 | 40 | 42 | 40.6 | 44.4 | 48.7 | 26.7 | 23.3 | 27.1 | 32.1 | 33 | 30 | 31 | 31 | 30.5 | 50 | 40 |  | 50 | 4
RAXAUL 132 | 90 | 106 | 108 | 112.2 | 122 | 101.6 | 108 | 115 | 88.8 | 64.6 | 57.2 | 0 | 0 | 0 | 24 | 100 | 98 | 111.8 | 105.4 | 91.6 | 72 | 55.4 | 55.2 | 61.8 | 59 | 71.8 | 42 | 84 | 97 | 113 | 120 |  | 122 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 42.3 | 52 | 51.4 | 50.8 | 55.4 | 45.2 | 39.1 | 37.3 | 66.5 | 66.2 | 67.9 | 63.6 | 68.1 | 74 | 76 | 77.6 | 72 | 71.1 | 74.6 | 71.8 | 61.2 | 57.5 | 61.8 | 63.6 | 68 | 66.8 | 66.8 | 66.6 | 69.7 | 70 | 70 |  | 77.6 | 37.3
Total IMPORT | 620.5 | 623.9 | 639.3 | 624.4 | 626.3 | 649.8 | 663.1 | 668.6 | 677.5 | 627.1 | 626.4 | 558.9 | 556.9 | 558.3 | 590.9 | 676.6 | 680 | 727.9 | 691.3 | 684.7 | 604.3 | 594.9 | 601.4 | 606.4 | 597.7 | 620.3 | 580.8 | 628.6 | 674.2 | 738 | 705 | 0 | 738 | 556.9
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | [31 empty] | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1289.79 | 1433.39 | 1550.89 | 1489.29 | 1536.69 | 1469.69 | 1407.29 | 1391.59 | 1394.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1350.19 | 1330.19 | 1406.99 | 1569.69 | 1602.29 | 1482.59 | 1443.09 | 1431.29 | 1440.89 | 1474.69 | 1307.69 | 2231.81 | 1602.29 | 1215.49
Interruption/Tripping | 0.29167: 150; 0.3125: 200; 0.33333: 200; 0.375: 200; 0.41667: 200; 0.45833: 100; 0.70833: 200; 0.72917: 250; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 250 |  | 250 | 100
TOTAL SYSTEM LOAD (EXPECTED) | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1289.79 | 1433.39 | 1550.89 | 1639.29 | 1736.69 | 1669.69 | 1607.29 | 1591.59 | 1494.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1550.19 | 1580.19 | 1656.99 | 1819.69 | 1852.29 | 1732.59 | 1693.09 | 1681.29 | 1440.89 | 1474.69 | 1307.69 | 1693.71 | 1852.29 | 1215.49
TOTAL NATIONAL LOAD (ACTUAL) | 1233.49 | 1235.69 | 1229.49 | 1215.49 | 1241.99 | 1276.29 | 1289.79 | 1433.39 | 1550.89 | 1639.29 | 1736.69 | 1669.69 | 1607.29 | 1591.59 | 1494.39 | 1544.19 | 1522.79 | 1551.99 | 1558.43 | 1575.73 | 1550.19 | 1580.19 | 1656.99 | 1819.69 | 1851.29 | 1732.59 | 1693.09 | 1681.29 | 1440.89 | 1474.69 | 1307.69 |  | 1851.29 | 1215.49
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0
NET IMPORT | 620.5 | 623.9 | 639.3 | 624.4 | 626.3 | 649.8 | 663.1 | 668.6 | 677.5 | 627.1 | 626.4 | 558.9 | 556.9 | 558.3 | 590.9 | 676.6 | 680 | 727.9 | 691.3 | 684.7 | 604.3 | 594.9 | 601.4 | 606.4 | 596.7 | 620.3 | 580.8 | 628.6 | 674.2 | 738 | 705 |  | 738 | 556.9
HZ | 50.02 | 49.963 | 50.025 | 50.006 | 50.043 | 50.059 | 50 | 49.914 | 49.9 | 50 | 49.955 | 50.04 | 50.068 | 50.014 | 50.019 | 49.993 | 50.02 | 50.01 | 50.02 | 49.96 | 50.05 | 50.06 | 50.06 | 50 | 49.92 | 49.968 | 50.06 | 50.06 | 50.012 | 49.917 | 50.001 |  | 50.068 | 49.9
HTD 132KV | 129.5 | 129.2 | 129 | 128.8 | 129 | 129 | 127 | 124.9 | 124.9 | 128 | 125.5 | 123.8 | 124.6 | 124.6 | 125.7 | 124.2 | 124.9 | 124.6 | 123.9 | 124.3 | 129.1 | 129 | 129 | 125.2 | 125.8 | 128.3 | 128.7 | 128.7 | 128.3 | 128.5 | 129.7 |  | 129.7 | 123.8
SUI 132KV | 132.8 | 132.5 | 132.9 | 132.1 | 132.1 | 132.1 | 130.5 | 128 | 128 | 129 | 127 | 125.7 | 127.1 | 127 | 127.8 | 127 | 127.6 | 127.3 | 126.8 | 127 | 131 | 131 | 131 | 126.8 | 127 | 129.9 | 130.2 | 130.2 | 130.4 | 131.5 | 132.8 |  | 132.9 | 125.7
DUBI 132KV | 128.7 | 130.2 | 129.3 | 128.4 | 128.4 | 128.4 | 127 | 125 | 125 | 129 | 125.6 | 126.5 | 127 | 127.8 | 124.6 | 125.8 | 128.5 | 124.6 | 125.9 | 125 | 128.8 | 129.7 | 129.7 | 126.4 | 130.8 | 130 | 129.3 | 129.3 | 129.9 | 128.5 | 129.7 |  | 130.8 | 124.6
ANAMANI 132KV | 130.9 | 132.2 | 131.7 | 131.2 | 131.2 | 131.2 | 130.5 | 129.2 | 129.2 | 130 | 125.9 | 126.5 | 126.8 | 127.9 | 125.6 | 127.5 | 129.7 | 126.5 | 127.4 | 125.8 | 128.7 | 129.7 | 129.7 | 125.4 | 129.9 | 132.3 | 131.7 | 131.7 | 133 | 131.8 | 131.1 |  | 133 | 125.4
KG-A 132KV | 131.9 | 132.4 | 132.8 | 131.4 | 131.4 | 131.4 | 132 | 129.2 | 129.2 | 134 | 132.7 | 131.8 | 134.6 | 134.1 | 134.4 | 132.6 | 132.8 | 133.4 | 132.2 | 132.1 | 138.6 | 134.2 | 134.2 | 130.7 | 133.8 | 134.8 | 135.6 | 135.6 | 134.9 | 131.4 | 132.8 |  | 138.6 | 129.2
KOHALPUR 132KV | 129.4 | 135.4 | 134.2 | 133.5 | 133.5 | 133.5 | 129.6 | 127.9 | 127.9 | 130.6 | 126.2 | 125.8 | 130.8 | 125.9 | 132.7 | 130.2 | 137.4 | 136.2 | 129.8 | 129 | 131.4 | 128.9 | 128.9 | 125.7 | 130.4 | 130.4 | 133.8 | 133.8 | 129.3 | 131 | 132.5 |  | 137.4 | 125.7
SUI 66KV | 66.5 | 66.7 | 66.7 | 66.4 | 66.9 | 66.9 | 65.7 | 64.3 | 64.3 | 65 | 63.8 | 63.1 | 63.8 | 63.8 | 64 | 63.9 | 63.9 | 64 | 63.7 | 64.8 | 66 | 66 | 66 | 63.2 | 63.9 | 65.5 | 65.2 | 65.2 | 65.4 | 66 | 66.8 |  | 66.9 | 63.1
[33 empty] | 0 | 0
Kathmandu Load | 160.939 | 145.057 | 136.867 | 136.238 | 145.84 | 173.44 | 188.44 | 233.24 | 319.04 | 374.44 | 388.44 | 373.22 | 351.732 | 349.24 | 42 | 322.74 | 309.36 | 321.16 | 316.46 | 327.88 | 338.44 | 328.54 | 347.04 | 414.22 | 437.26 | 403.227 | 381.94 | 381.94 | 329.84 | 228.14 | 209.94 |  | 437.26 | 42
MRS-SYU | -13 | -13.9 | -16.7 | -18.6 | -13.8 | -6.9 | -7.6 | -5 | 18.9 | 31 | 28.9 | 40 | 33.3 | 34.5 | 32.1 | 23.1 | 20.2 | 22.2 | 15.9 | 25.2 | 31 | 28 | 26.5 | 34.7 | 45.3 | 40.1 | 35.7 | 35.7 | 26 | 7.4 | 0.3 | 75 | 45.3 | -18.6
NMRS-MATA | -22.6 | -22.3 | -27.4 | -30.1 | -21.4 | -13 | -13.9 | -12 | 19.7 | 41.4 | 39.6 | 55.5 | 46 | 48.6 | 40.1 | 25.8 | 21.9 | 25.6 | 16 | 28 | 40 | 38.3 | 35.7 | 45.2 | 58.7 | 51.7 | 45.7 | 45.7 | 31.2 | 4.5 | -4.6 | 240 | 58.7 | -30.1
KL2-MATA | -8.2 | -13 | -12.5 | -11.6 | -13.7 | -6 | -1.5 | 7.2 | 24 | 43 | 47 | 29.1 | 23.3 | 19.3 | 29 | 20.9 | 22 | 26 | 28 | 26 | 40 | 40 | 45 | 61 | 66 | 60.1 | 50 | 50 | 42 | 7 | -2 | 240 | 66 | -13.7
KL1-SYU | -2.5 | -5.3 | -8.1 | -7.2 | -5.1 | -3.5 | -1.6 | -0.8 | 7.6 | 24.3 | 25.6 | 21.5 | 19.2 | 19.4 | 15 | 7 | 5.9 | 4.7 | 5.2 | 9.5 | 21.6 | 21 | 23.2 | 28.2 | 29.5 | 28.3 | 25.9 | 25.9 | 16 | 4.6 | 1.6 | 60 | 29.5 | -8.1
KHIMTI-LAMOSANGHU | 116.399 | 108.717 | 113.727 | 115.898 | 112 | 115 | 125 | 155 | 160 | 145 | 155 | 131.68 | 131.692 | 123 | 114.636 | 139.4 | 141.12 | 148.32 | 160.32 | 151.84 | 119.2 | 115.2 | 131.2 | 159.68 | 152.32 | 138.387 | 140 | 140 | 130 | 120 | 130 | 120 | 160.32 | 108.717
LAMOSHANGU-BHAKTAPUR | 80.6 | 76.8 | 80.4 | 81.2 | 76.3 | 79.6 | 88.4 | 99.2 | 97.4 | 88.7 | 96.2 | 89.6 | 88.2 | 79.6 | 81 | 90.8 | 94.7 | 90.8 | 103 | 98.8 | 81.7 | 79.7 | 86.6 | 99.9 | 97.5 | 90 | 86.5 | 86.5 | 90.9 | 82.5 | 74
BALAJU-SYUCHATAR | 70 | 69.4 | 76.2 | 78.6 | 67.9 | 55.5 | 56.4 | 58.3 | 18.4 | -22.8 | -15 | -24.9 | -12.8 | -18.7 | -6.9 | 17.9 | 23.9 | 14.4 | 32.6 | 18.2 | -17.2 | -17.1 | -13.8 | -29 | -50 | -45.4 | -35 | -35 | -5.6 | 40 | 55
DHALKE-NAWALPUR I | 88.8 | 81.3 | 89.4 | 90.5 | 82.5 | 85.9 | 96.22 | 106.8 | 93.6 | 80.3 | 87.1 | 83.9 | 94.9 | 95 | 75.9 | 85.3 | 93.3 | 88.9 | 102 | 93.1 | 73.1 | 74.1 | 79.7 | 85.7 | 84.5 | 80.7 | 72 | 72 | 83 | 79.5 | 81 |  | 106.8 | 72
N. BHARATPUR-BARDGHAT I | 28.4 | -30.4 | 29.1 | 31.2 | 30.5 | 19.8 | 21.2 | 22.8 | 2.5 | -5.2 | -5.1 | -18.2 | -9.7 | -9.6 | -9 | -2.6 | 0 | 0 | 9 | 3.7 | -5.9 | -4.4 | -4 | -6.2 | -14.1 | -7.4 | -3 | -3 | -1 | 15 | 16 |  | 31.2 | -30.4
DAMAK-DUHABI | -8.1 | -7.5 | -7.2 | -7.3 | -8.5 | -11.5 | -18 | -23 | -31.6 | -39.5 | -41.9 | -41.6 | -32.9 | -29.5 | -24.2 | -25.1 | -27.6 | -29.7 | -24.7 | -28.5 | -38.2 | -39.5 | -50 | -54.5 | -51.7 | -37.9 | -32 | -32 | -27 | -13 | -8.8 |  | -7.2 | -54.5
HETAUDA-KAMANE | -27.8 | -23.8 | -27.2 | -27.1 | -22.6 | -23.4 | -29.7 | -36.5 | -26.6 | -27.3 | -31.7 | -9.4 | -11.5 | -10.2 | -26 | -26.5 | -29.9 | -28.6 | -36.3 | -26.6 | -27.7 | -29.5 | -33.4 | -41.4 | -36.1 | 33.8 | -30 | -30 | -40.5 | -26 | -23 |  | 33.8 | -41.4
MIRCHAIYA LAHAN 2 | 93.8 | 84.4 | 87.7 | 86.2 | 86.2 | 95.9 | 97.8 | 100.6 | 109.6 | 102 | 106.4 | 100.3 | 92.8 | 86.3 | 89.8 | 109.9 | 107.4 | 120.1 | 107.4 | 118.1 | 100.1 | 96.7 | 104.9 | 117.3 | 115.1 | 100.8 | 109 | 109 | 107 | 100.5 | 96 |  | 120.1 | 84.4
Water Level
UTK | 1983.7 | 1983.97 | 1984.22 | 1984.42 | 1984.62 | 1984.85 |  | 1984.95 |  | 1984.72 |  | 1984.6 | 1984.45 | 1984.47 | 1984.57 |  |  | 1984.4 | 1984.28 | 1984 | 1983.8 |  | 1983.88 |  | 1983.67 |  | 1983.18 | 1983.15 | 1983.15 | 1983.18 | 1983.35
KGA | 520.23 | 520.6 | 520.94 | 521.26 | 521.57 | 521.86 |  | 522.14 |  | 522.22 |  | 522 | 521.57 | 521.3 | 521.06 | 520.8 |  | 520.52 | 520.43 | 520.36 | 520.21 |  | 520.14 |  | 519.8 |  | 519.43 |  | 519.44 | 519.65 | 519.95
MMRS | 622.12 | 622.18 | 622.4 | 622.79 | 623.13 | 623.01 |  | 622.85 |  | 622.9 |  | 622.82 | 622.64 | 622.59 | 622.45 | 622.36 |  | 622.13 | 622.06 | 621.79 | 621.88 |  | 621.95 |  | 621.88 |  | 621.91 |  | 622 | 622.12 | 622.22
MRS | 335.02 | 335.38 | 335.72 | 336.05 | 336.37 | 336.62 |  | 336.85 |  | 336.76 |  | 336.61 | 336.4 | 336.17 | 335.97 | 335.91 |  | 335.99 | 336.04 | 336.01 | 335.92 |  | 335.93 |  | 335.8 |  | 335.4 |  | 335.12 | 335.5 | 335.11
CHM | 883.6 | 884.3 | 884.9 | 885.5 | 886 | 886.5 |  | 886.9 |  | 887 |  | 886.8 | 886.5 | 886.4 | 886.4 | 886.3 |  | 885.9 | 885.9 | 885.8 | 885.7 |  | 885.6 |  | 884.6 |  | 883.1 |  | 882.7 | 882.8 | 882.7
KL 1 | 0: 1519.47; 0.20833: 1519.48; 0.33333: 1519.48
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1736.69; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/15)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 16
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/16 |  |  | 2080/10/16 |  |  | Wednesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 609 | 624 | 596.4 | 592.5 | 671.1 | 650.2 | 618.8 | 610.9 | 458.6 | 327.9 | 291.9 | 544.1 | 570.2 | 614.1 | 640.9 | 685.9 | 700.3 | 705.7 | 722 | 622.3 | 604.7 | 602.6 | 607.8 | 590.6 | 337 | 568.6 | 592.3 | 656.6 | 668.6 | 670.9 | 609
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1698MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1192 | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1312.19 | 1334.49 | 1530.49 | 1498.29 | 1607.79 | 1698.49 | 1523.69 | 1483.39 | 1580.39 | 1470.49 | 1483.09 | 1497.72 | 1485.38 | 1500.17 | 1466 | 1485.99 | 1547.59 | 1802.05 | 1840.95 | 1752.99 | 1628.89 | 1608.69 | 1656.19 | 1418.19 | 1306.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1840.95 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1840.95 MW
Solu Khola Dudhkoshi(86) | 26.9 | 26.9 | 26.9 | 28.4 | 28.4 | 28.4 | 28.4 | 27.2 | 27.2 | 27.2 | 27.3 | 27.3 | 27.3 | 27.3 | 27 | 27 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.8 | 27.8 | 27.8 | 25.1 | 86 | 28.4 | 25.1
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 16
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9.9 | 9.9 | 9.9 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 10.7 | 10.4 | 10.4 | 10 | 54 | 10.7 | 8.2 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/16)
Likhu-IV(52.4) | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 14.5 | 14.5 | 14.5 | 15 | 52.4 | 15 | 12.3
Upper Marsyangdi "A"(50) | 28.9 | 28.9 | 28.9 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 28.4 | 28.3 | 28.3 | 27.9 | 50 | 28.9 | 27.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | [25 empty] | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 15.9 | 15.9 | 16.6 | 45 | 16.6 | 15.3 |  | IPP | 464.85 | 464.85 | 464.85 | 462.95 | 462.95 | 462.95 | 461.65 | 461.65 | 459.35 | 459.35 | 459.35 | 459.05 | [25 empty] | 459.05 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 473.15 | 473.15 | 468.05
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.3 | 35.3 | 35.3 | 36 | 36 | 36 | 91 | 271.3 | 416.5 | 111.6 | 51.6 | 111.5 | [25 empty] | 106.5 | 86.6 | 96.6 | 96.6 | 96.6 | 96.6 | 51.6 | 201.6 | 101.6 | 100.5 | 100.5 | 35.5
Mistri Khola(42) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7.5 | 8 | 8 | 7 | 42 | 8 | 6.5 |  | NEA ROR PROR | 103.54 | 103.54 | 103.54 | 101.04 | 101.04 | 101.04 | 163.04 | 306.74 | 330.74 | 228.64 | 232.24 | 245.74 | [25 empty] | 264.04 | 251.34 | 241.57 | 224.83 | 224.32 | 237.85 | 184.14 | 339.5 | 249.44 | 175.94 | 175.94 | 132.24
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 609 | 609 | 624 | 596.4 | 592.5 | 671.1 | 618.8 | 458.6 | 291.9 | 544.1 | 570.2 | 614.1 | [25 empty] | 640.9 | 685.9 | 700.3 | 705.7 | 722 | 622.3 | 602.6 | 590.6 | 568.6 | 656.6 | 668.6 | 670.9
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 180 | 170 | 150 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 50 | 250 | 250 | 250 | 250 | 0 | 0
Nyadi(30) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.8 | 7.8 | 7.8 | 7.6 | 30 | 7.8 | 7.2 |  | System_Load | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1334.49 | 1498.29 | 1698.49 | 1523.69 | 1483.39 | 1580.39 | [25 empty] | 1470.49 | 1483.09 | 1497.72 | 1486.38 | 1502.17 | 1466 | 1547.59 | 1840.95 | 1628.89 | 1656.19 | 1418.19 | 1306.69
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0 | 0 | 0 | -1 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 6.8 | 6.8 | 6.8 | 7.5 | 28 | 7.5 | 6.8 |  | National_Load | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1334.49 | 1498.29 | 1698.49 | 1523.69 | 1483.39 | 1580.39 | [25 empty] | 1470.49 | 1483.09 | 1497.72 | 1485.38 | 1500.17 | 1466 | 1547.59 | 1840.95 | 1628.89 | 1656.19 | 1418.19 | 1306.69
Dordi(27) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 5.4 | 5.7 | 5.7 | 6.4 | 30 | 6.4 | 5.4
Upper Madi(25) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 8.3 | 8.3 | 8.3 | 6.4 | 25 | 8.3 | 6.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 7.2 | 7.2 | 7 | 25 | 7.2 | 6.9
Solu Khola(23.5) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.1 | 6.9 | 6.9 | 6.9 | 23.5 | 7.5 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 10.6 | 11 | 11 | 10.1 | 22 | 11 | 6.2
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 17.5 | 17.5 | 17.5 | 23.9 | 23.9 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 20.1 | 20.1 | 20.1 | 20.1 | 21 | 21.6 | 21.6 | 21.6 | 18.5 | 16.6 | 17 | 14.6 | 14.6 | 13.5 | 13.5 | 16.7 | 17.5 | 17.5 | 20.9 | 240 | 23.9 | 13.5
Total IPP | 464.85 | 464.85 | 464.85 | 462.95 | 462.95 | 462.95 | 462.95 | 461.65 | 461.65 | 461.65 | 459.35 | 459.35 | 459.35 | 459.35 | 459.05 | 459.05 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 459.25 | 471.65 | 473.15 | 473.15 | 468.05 | 1042.4 | 473.15 | 459.05
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 140 | 235 | 330 | 380 | 75 | 15 | 75 | 70 | 50 | 60 | 60 | 60 | 60 | 15 | 15 | 145 | 165 | 345 | 65 | 65 | 65 | 65 | 0 | 456 | 380 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.3 | 8.3 | 8.3 | 9 | 9 | 9 | 9 | 9 | 9 | 9.3 | 9 | 9.5 | 9.6 | 9.6 | 9.5 | 9.5 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 8.6 | 8.5 | 8.5 | 8.5 | 22.1 | 9.6 | 8.3
Total NEA SUBSIDIARIES | 35.3 | 35.3 | 35.3 | 36 | 36 | 36 | 36 | 91 | 176 | 271.3 | 366 | 416.5 | 111.6 | 51.6 | 111.5 | 106.5 | 86.6 | 96.6 | 96.6 | 96.6 | 96.6 | 51.6 | 51.6 | 181.6 | 201.6 | 381.6 | 101.6 | 100.6 | 100.5 | 100.5 | 35.5 | 538.1 | 416.5 | 35.3
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 112 | 132 | 117.1 | 132 | 63.5 | 63.1 | 63.5 | 70.9 | 61.3 | 61.3 | 61.3 | 61.3 | 61.3 | 31 | 45.2 | 111 | 141 | 141 | 92.1 | 40.6 | 30.5 | 30.5 | 0 | 144 | 141 | 0
Middle MRS(70) | 22.8 | 22.8 | 22.8 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 35 | 35.2 | 34.8 | 35 | 22.9 | 22.9 | 23 | 34.8 | 34.8 | 34.8 | 28.5 | 28.5 | 35 | 26 | 26 | 35 | 35 | 35 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 70 | 35.2 | 21.9
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 45 | 49 | 59.9 | 69 | 51.9 | 51.8 | 51.8 | 35.9 | 33.4 | 33.4 | 33.4 | 33.4 | 46 | 34 | 34 | 68 | 68 | 47 | 33.2 | 33.6 | 33.8 | 33.8 | 16.3 | 69 | 69 | 0
U Trisuli 3A(60) | 38.3 | 38.3 | 38.3 | 36 | 36 | 36 | 36 | 36 | 36.8 | 36.3 | 36.3 | 36.4 | 36.3 | 36.3 | 36.3 | 38 | 38 | 38 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 33 | 35 | 35 | 38.3 | 60 | 38.3 | 33
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10.4 | 11 | 10 | 0 | 0 | 10 | 22.5 | 23.2 | 15 | 10 | 15 | 15 | 0 | 0 | 10.5 | 14.6 | 23.2 | 10.4 | 10.3 | 0 | 0 | 0 | 30 | 23.2 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 2.3 | 5.2 | 10.9 | 15 | 18 | 18.6 | 18 | 16.43 | 12.69 | 7.18 | 1.61 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.6 | 0 | [14 empty] | Tanakpur | 50 | 60 | 56.9 | 59 | 62.5 | 66.6 | 63.7 | 63 | 61.9 | 64.5 | 59 | 61.2 | 64.9 | 71.2 | 66 | 73 | 59.3 | 62.3 | 69.6 | 61.2 | 67.9 | 65.4 | 65.8 | 55
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 4 | 4 | [14 empty] | Muz | 380 | 405 | 380 | 371 | 451 | 401 | 249 | 121 | 384.2 | 401 | 426 | 387 | 408.4 | 413 | 440 | 444 | 389 | 419 | 368 | 377.1 | 410 | 405 | 400 | 392
DEVI(14.1) | 10.1 | 10.1 | 10.1 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 11 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 9.5 | 9.5 | 9.5 | 10.5 | 14.1 | 11 | 9.5 | [14 empty] | Ram | 4 | 4 | 6 | 6 | 6 | 5 | 6 | 4 | 3 | 3 | 3 | 33 | 41.3 | 50 | 50 | 46 | 35 | 32 | 38 | 29.7 | 36 | 40 | 40 | 4
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 14 | 3.3 | 3.3 | [14 empty] | Rax | 120 | 108 | 102.3 | 102.8 | 100.6 | 99.7 | 68 | 35 | 31 | 28 | 50 | 95 | 105 | 97 | 84 | 98 | 87 | 42 | 60 | 45 | 83 | 100 | 109 | 108
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 55 | 47 | 51.2 | 53.7 | 51 | 46.5 | 71.9 | 68.9 | 64 | 73.7 | 76.1 | 64.7 | 66.3 | 69.1 | 65.7 | 61 | 52 | 47.3 | 55 | 55.6 | 59.7 | 58.2 | 56.1 | 50
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 50 | 60 | 56.9 | 59 | 62.5 | 66.6 | 63.7 | 63 | 61.9 | 64.5 | 59 | 61.2 | 64.9 | 71.2 | 66 | 73 | 59.3 | 62.3 | 69.6 | 61.2 | 67.9 | 65.4 | 65.8 | 55
Total ROR | 103.54 | 103.54 | 103.54 | 101.04 | 101.04 | 101.04 | 163.04 | 163.04 | 281.94 | 306.74 | 304.54 | 330.74 | 228.64 | 232.24 | 245.74 | 264.04 | 251.34 | 241.57 | 224.83 | 224.32 | 237.85 | 170.44 | 184.14 | 303.4 | 339.5 | 325.14 | 249.44 | 194.14 | 175.94 | 175.94 | 132.24 | 489.91 | 339.5 | 101.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [15 empty] | 380 | 405 | 380 | 371 | 451 | 401 | 249 | 121 | 384.2 | 401 | 426 | 387 | 408.4 | 413 | 440 | 444 | 389 | 419 | 368 | 377.1 | 410 | 405 | 400 | 392
KL2(32) | [31 empty] | 32 | 0 | 0 | [15 empty] | 4 | 4 | 6 | 6 | 6 | 5 | 6 | 4 | 3 | 3 | 3 | 33 | 41.3 | 50 | 50 | 46 | 35 | 32 | 38 | 29.7 | 36 | 40 | 40 | 4
KL3(14) | [31 empty] | 14 | 0 | 0 | [15 empty] | 120 | 108 | 102.3 | 102.8 | 100.6 | 99.7 | 68 | 35 | 31 | 28 | 50 | 95 | 105 | 97 | 84 | 98 | 87 | 42 | 60 | 45 | 83 | 100 | 109 | 108
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | [15 empty] | 55 | 47 | 51.2 | 53.7 | 51 | 46.5 | 71.9 | 68.9 | 64 | 73.7 | 76.1 | 64.7 | 66.3 | 69.1 | 65.7 | 61 | 52 | 47.3 | 55 | 55.6 | 59.7 | 58.2 | 56.1 | 50
TANAKPUR | 55 | 50 | 60 | 56.9 | 59 | 62.5 | 65.6 | 66.6 | 57.8 | 63.7 | 63.2 | 63 | 61.9 | 64.5 | 59 | 61.2 | 64.9 | 71.2 | 66 | 73 | 59.3 | 73.1 | 62.3 | 62.6 | 69.6 | 58 | 61.2 | 64.3 | 67.9 | 65.4 | 65.8 |  | 73.1 | 50
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 392 | 380 | 405 | 380 | 371 | 451 | 420 | 401 | 400 | 249 | 152 | 121 | 384.2 | 401 | 426 | 387 | 408.4 | 413 | 440 | 444 | 389 | 422 | 419 | 400 | 368 | 146 | 377.1 | 392.8 | 410 | 405 | 400 |  | 451 | 121
RAMNAGAR | 4 | 4 | 4 | 6 | 6 | 6 | 4 | 5 | 6 | 6 | 6 | 4 | 3 | 3 | 3 | 33 | 41.3 | 50 | 50 | 46 | 35 | 30 | 32 | 40 | 38 | 38 | 29.7 | 35 | 36 | 40 | 40 |  | 50 | 3 | [22 empty] | 50 | 0 | 380 | 4 | 120 | 55
RAXAUL 132 | 108 | 120 | 108 | 102.3 | 102.8 | 100.6 | 107 | 99.7 | 103.2 | 68 | 34.6 | 35 | 31 | 28 | 50 | 95 | 105 | 97 | 84 | 98 | 87 | 31 | 42 | 54 | 60 | 43 | 45 | 44.6 | 83 | 100 | 109 |  | 120 | 28 | [22 empty] | 60 | 0 | 405 | 4 | 108 | 47
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 56.9 | 0 | 380 | 6 | 102.3 | 51.2
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 59 | 0 | 371 | 6 | 102.8 | 53.7
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 62.5 | 0 | 451 | 6 | 100.6 | 51
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 66.6 | 0 | 401 | 5 | 99.7 | 46.5
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 63.7 | 0 | 249 | 6 | 68 | 71.9
SAMPATIYA 132 kV | 50 | 55 | 47 | 51.2 | 53.7 | 51 | 53.6 | 46.5 | 43.9 | 71.9 | 72.1 | 68.9 | 64 | 73.7 | 76.1 | 64.7 | 66.3 | 69.1 | 65.7 | 61 | 52 | 48.6 | 47.3 | 51.2 | 55 | 52 | 55.6 | 55.6 | 59.7 | 58.2 | 56.1 |  | 76.1 | 43.9 | [22 empty] | 63 | 0 | 121 | 4 | 35 | 68.9
Total IMPORT | 609 | 609 | 624 | 596.4 | 592.5 | 671.1 | 650.2 | 618.8 | 610.9 | 458.6 | 327.9 | 291.9 | 544.1 | 570.2 | 614.1 | 640.9 | 685.9 | 700.3 | 705.7 | 722 | 622.3 | 604.7 | 602.6 | 607.8 | 590.6 | 337 | 568.6 | 592.3 | 656.6 | 668.6 | 670.9 | 0 | 722 | 291.9 | [22 empty] | 61.9 | 0 | 384.2 | 3 | 31 | 64
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 64.5 | 0 | 401 | 3 | 28 | 73.7
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 59 | 0 | 426 | 3 | 50 | 76.1
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 61.2 | 0 | 387 | 33 | 95 | 64.7
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0 | [22 empty] | 64.9 | 0 | 408.4 | 41.3 | 105 | 66.3
TOTAL SYSTEM LOAD (ACTUAL) | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1312.19 | 1334.49 | 1530.49 | 1498.29 | 1457.79 | 1498.49 | 1343.69 | 1313.39 | 1430.39 | 1470.49 | 1483.09 | 1497.72 | 1486.38 | 1502.17 | 1416 | 1285.99 | 1297.59 | 1552.05 | 1590.95 | 1502.99 | 1378.89 | 1358.69 | 1406.19 | 1418.19 | 1306.69 | 2231.81 | 1590.95 | 1192.49 | [22 empty] | 71.2 | 0 | 413 | 50 | 97 | 69.1
Interruption/Tripping | 0.3125: 150; 0.33333: 200; 0.375: 180; 0.41667: 170; 0.45833: 150; 0.70833: 50; 0.72917: 200; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 250; 0.875: 250; 0.91667: 0; 0.95833: 0 |  | 250 | 0 | [22 empty] | 66 | 0 | 440 | 50 | 84 | 65.7
TOTAL SYSTEM LOAD (EXPECTED) | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1312.19 | 1334.49 | 1530.49 | 1498.29 | 1607.79 | 1698.49 | 1523.69 | 1483.39 | 1580.39 | 1470.49 | 1483.09 | 1497.72 | 1486.38 | 1502.17 | 1466 | 1485.99 | 1547.59 | 1802.05 | 1840.95 | 1752.99 | 1628.89 | 1608.69 | 1656.19 | 1418.19 | 1306.69 | 1693.71 | 1840.95 | 1192.49 | [22 empty] | 73 | 0 | 444 | 46 | 98 | 61
TOTAL NATIONAL LOAD (ACTUAL) | 1212.69 | 1212.69 | 1227.69 | 1196.39 | 1192.49 | 1271.09 | 1312.19 | 1334.49 | 1530.49 | 1498.29 | 1607.79 | 1698.49 | 1523.69 | 1483.39 | 1580.39 | 1470.49 | 1483.09 | 1497.72 | 1485.38 | 1500.17 | 1466 | 1485.99 | 1547.59 | 1802.05 | 1840.95 | 1752.99 | 1628.89 | 1608.69 | 1656.19 | 1418.19 | 1306.69 |  | 1840.95 | 1192.49 | [22 empty] | 59.3 | 0 | 389 | 35 | 87 | 52
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 62.3 | 0 | 419 | 32 | 42 | 47.3
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 69.6 | 0 | 368 | 38 | 60 | 55
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61.2 | 0 | 377.1 | 29.7 | 45 | 55.6
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67.9 | 0 | 410 | 36 | 83 | 59.7
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 65.4 | 0 | 405 | 40 | 100 | 58.2
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | [22 empty] | 65.8 | 0 | 400 | 40 | 109 | 56.1
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | [22 empty] | 55 | 0 | 392 | 4 | 108 | 50
NET IMPORT | 609 | 609 | 624 | 596.4 | 592.5 | 671.1 | 650.2 | 618.8 | 610.9 | 458.6 | 327.9 | 291.9 | 544.1 | 570.2 | 614.1 | 640.9 | 685.9 | 700.3 | 704.7 | 720 | 622.3 | 604.7 | 602.6 | 607.8 | 590.6 | 337 | 568.6 | 592.3 | 656.6 | 668.6 | 670.9 |  | 720 | 291.9
HZ | 50.058 | 49.962 | 49.893 | 50.054 | 50.046 | 50.01 | 49.965 | 49.909 | 49.832 | 50.029 | 50.035 | 50.152 | 50.094 | 50.001 | 49.989 | 49.901 | 50.011 | 50.067 | 50.03 | 49.97 | 49.97 | 49.985 | 50.036 | 49.941 | 49.877 | 49.934 | 49.99 | 49.99 | 50.02 | 50.03 | 49.99 |  | 50.152 | 49.832
HTD 132KV | 130.8 | 130.7 | 129 | 129.999 | 130.7 | 127.1 | 127.4 | 126.7 | 122.8 | 127.2 | 127 | 126.6 | 124.9 | 126 | 123.9 | 126.4 | 125.6 | 125 | 123.9 | 124.6 | 127.9 | 127.4 | 125.9 | 125.5 | 125.2 | 127.1 | 128.3 | 128.3 | 127 | 127.5 | 128.3 |  | 130.8 | 122.8
SUI 132KV | 134 | 134 | 133 | 133.5 | 133.9 | 130.7 | 129.99 | 129.9 | 125.9 | 128.8 | 128.3 | 128 | 127 | 128 | 126.5 | 129.3 | 128.9 | 128.5 | 127 | 128 | 130.8 | 130.2 | 128.9 | 127.8 | 127.4 | 129.5 | 130.6 | 130.6 | 130.1 | 131.2 | 132.6 |  | 134 | 125.9
DUBI 132KV | 130.1 | 131.2 | 128 | 130 | 128.5 | 124.7 | 128 | 123.2 | 122.7 | 128.8 | 127.8 | 127.8 | 130.2 | 126.3 | 125.1 | 126.3 | 125.9 | 128.1 | 126.5 | 124.6 | 128.8 | 126.9 | 127.1 | 128.2 | 128.9 | 131.2 | 132.6 | 132.6 | 127.3 | 128 | 129.5 |  | 132.6 | 122.7
ANAMANI 132KV | 132.7 | 133 | 130 | 133.1 | 130.2 | 128.9 | 131.7 | 127.8 | 125.9 | 130.1 | 128.2 | 128.1 | 130.8 | 126.3 | 125.1 | 127.6 | 126.2 | 129.5 | 127 | 125.6 | 128.8 | 126 | 124.7 | 125.9 | 127.3 | 130.6 | 133.5 | 133.5 | 129.4 | 129.1 | 131.7 |  | 133.5 | 124.7
KG-A 132KV | 133.5 | 135.8 | 132 | 131.8 | 132 | 128.3 | 132.1 | 132.1 | 130.9 | 136.5 | 136 | 135.8 | 132.1 | 133 | 132.4 | 135.6 | 134.9 | 135 | 133.6 | 133.7 | 135.2 | 135.4 | 134.5 | 134.7 | 133.7 | 135 | 137.8 | 137.8 | 133.3 | 132.8 | 131.4 |  | 137.8 | 128.3
KOHALPUR 132KV | 132.6 | 132.6 | 127 | 133.8 | 132.3 | 130.7 | 126.8 | 126.6 | 125.9 | 128.6 | 127.5 | 131.35 | 130.6 | 129.1 | 127.4 | 131.2 | 133.4 | 131.7 | 132 | 124 | 133.1 | 134.6 | 135 | 134.4 | 130.9 | 133 | 130.2 | 130.2 | 132.7 | 128.7 | 10.6 |  | 135 | 10.6
SUI 66KV | 67.5 | 67.6 | 67 | 67.1 | 67.6 | 66 | 65.9 | 65.3 | 63.3 | 64.6 | 64.2 | 64 | 63.7 | 64.1 | 63.4 | 64.8 | 64.7 | 64.2 | 63.6 | 64.3 | 65.6 | 65.2 | 64.5 | 63.9 | 63.8 | 65.1 | 65.1 | 65.1 | 65.1 | 66 | 66.8 |  | 67.6 | 63.3
[33 empty] | 0 | 0
Kathmandu Load | 152.94 | 145.04 | 120.54 | 134.588 | 142.888 | 177.144 | 206.36 | 241.596 | 319.716 | 353.104 | 374.6 | 377.044 | 359.03 | 336.822 | 42 | 313.025 | 300.302 | 293.67 | 278.43 | 293.52 | 302.05 | 314.54 | 346.84 | 407.2 | 427.9 | 404.82 | 375.08 | 356.44 | 321.46 | 238.34 | 185.48 |  | 427.9 | 42
MRS-SYU | -4 | -6 | -15 | -13 | -11.6 | -16 | -5.4 | 6 | 17.5 | 23.6 | 29.6 | 32 | 21 | 26 | 25.6 | 23.9 | 21 | 21 | 18 | 16 | 28 | 17.1 | 18 | 36 | 39.2 | 37.1 | 30.4 | 20.1 | 20.1 | 8.1 | 1.2 | 75 | 39.2 | -16
NMRS-MATA | -9.6 | -11.5 | -25 | -20.6 | -18.9 | -24.5 | -11.2 | 3.1 | 16.9 | 31.1 | 38.1 | 43.3 | 28.6 | 34 | 27.9 | 30.1 | 24.7 | 25 | 17 | 17.6 | 34.7 | 22 | 23.1 | 46.5 | 50.6 | 50.3 | 40.5 | 27.1 | 20.1 | 7 | -2.5 | 240 | 50.6 | -25
KL2-MATA | -10 | -14 | -9 | -13.1 | -9.6 | 3 | 3.6 | 6.4 | 25.2 | 39.6 | 44.5 | 43.9 | 44 | 31 | 27 | 15.4 | 12.3 | 14 | 18 | 19 | 28 | 42 | 50 | 58 | 63 | 53 | 57 | 54.9 | 43.1 | 13 | -3.3 | 240 | 63 | -14
KL1-SYU | -4 | -4 | -6 | -7.2 | -1.4 | 0.9 | -1.6 | 1.2 | 4.9 | 21.1 | 24.9 | 22.1 | 20 | 17 | 8.1 | 7.8 | 2.6 | 2 | 4 | 5 | 9 | 21 | 23 | 28 | 30 | 28 | 28.2 | 26.7 | 13.8 | 3 | -2.7 | 60 | 30 | -7.2
KHIMTI-LAMOSANGHU | 90 | 90 | 85 | 99.548 | 95.448 | 124.804 | 132.02 | 135.956 | 165.476 | 147.764 | 145.96 | 141.204 | 145.29 | 124.582 | 147.962 | 126.085 | 131.262 | 124.8 | 120 | 140 | 112 | 123.2 | 144 | 145.6 | 152 | 147.68 | 130.24 | 142.4 | 137.12 | 120 | 101.44 | 120 | 165.476 | 85
LAMOSHANGU-BHAKTAPUR | 71 | 70 | 74 | 72.3 | 70 | 84 | 88 | 90.4 | 105.1 | 96 | 96.2 | 93.1 | 93.2 | 76.7 | 88.9 | 83.1 | 86.2 | 86 | 89 | 90 | 78 | 84 | 94 | 94 | 98.3 | 95.6 | 86.4 | 94 | 91.8 | 84.2 | 75.9 |  | 105.1 | 70
BALAJU-SYUCHATAR | 60 | 65 | 68 | 66.2 | 61.3 | 66.3 | 55.3 | 43.3 | 25.7 | -6.9 | -21.8 | -21.6 | -2.8 | -5 | 10.1 | 10.5 | 18.9 | 21 | 24 | 25 | -8 | -3 | -3 | -30 | -35.4 | -28 | -36.8 | -9 | 6.1 | 32 | 41.6 |  | 68 | -36.8
DHALKE-NAWALPUR I | 72 | 72 | 78 | 73 | 75 | 90.4 | 94.3 | 87.8 | 105.2 | 82.5 | 73.5 | 66.5 | 88.7 | 78.3 | 92.4 | 85.1 | 90.2 | 89 | 93 | 100 | 80 | 87 | 90 | 90 | 97 | 78.1 | 84.6 | 96.9 | 92 | 83 | 81 |  | 105.2 | 66.5
N. BHARATPUR-BARDGHAT I | 18.5 | 23.5 | 27 | 28.4 | 28.7 | 30.6 | 27.7 | 22.1 | 12.1 | 7 | 1.8 | -2.5 | 8.3 | 4.2 | 6.8 | -4.1 | 0 | 0 | 3 | 3 | 1 | 7 | 8 | -3.3 | -14 | -21 | -2.9 | 6.5 | 13.3 | 17.8 | 21.2 |  | 30.6 | -21
DAMAK-DUHABI | -9.4 | -7 | -6.1 | -5.3 | -4.9 | -13.4 | -19.7 | -23 | -29 | -38.9 | -43.2 | -40.6 | -28.8 | -27.2 | -25.5 | -20.3 | -20.2 | -18 | -30 | -28 | -30.1 | -45 | -53.1 | -62 | -55 | -47.4 | -37.1 | -33.6 | -26 | -20.9 | -12.2 |  | -4.9 | -62
HETAUDA-KAMANE | -21 | -20 | -25 | -25.1 | -24 | -38 | -35.4 | -29.2 | -33.7 | -34.9 | -33.5 | -29.3 | -38.2 | -27.1 | -32.9 | -16.5 | -19.6 | -23 | -27 | -27 | -28 | -38 | -44 | -35 | -39 | -30 | -36.9 | -45.5 | -46.1 | -28 | -21.5 |  | -16.5 | -46.1
MIRCHAIYA LAHAN 2 | 93.4 | 85 | 88 | 84 | 85.7 | 85.6 | 97.2 | 104.1 | 108.8 | 101.4 | 99.6 | 97.3 | 90.5 | 98.9 | 103.6 | 111.8 | 102.2 | 109 | 118 | 118 | 94 | 99 | 106.3 | 119 | 111.2 | 103 | 90.41 | 87.3 | 96 | 100.5 | 97.8 |  | 119 | 84
Water Level
UTK | 1983.6 | 1983.88 | 1984.1 | 1984..32 | 1984.55 | 1984.75 |  | 1984.9 |  | 1984.72 |  | 1984.08 | 1983.73 | 1983.77 | 1983.97 | 1983.97 | 1583.98 | 1984 | 1984.02 | 1984.07 | 1984.12 |  | 1984.28 |  | 1984.1 |  | 1983.38 |  | 1983.41 | 1983.44 | 1983.62
KGA | 520.32 | 520.68 | 520.96 | 521.38 | 521.65 | 521.96 |  | 522.1 |  | 521.85 |  | 521.38 | 521.16 | 521.08 | 521 | 520.88 | 520.76 | 520.7 | 520.61 | 520.53 | 520.46 |  | 520.56 |  | 520.14 |  | 519.55 |  | 519.54 | 519.65 | 519.88
MMRS | 622.31 | 622.42 | 622.95 | 623.03 | 623.08 | 623.15 |  | 623.1 |  | 623.02 |  | 622.86 | 622.83 | 622.85 | 622.88 | 622.8 | 622.6 | 622.51 | 622.47 | 622.5 | 622.455 |  | 622.51 |  | 622.47 |  | 622.35
MRS | 335.43 | 335.71 | 336 | 336.24 | 336.49 | 336.72 |  | 336.82 |  | 336.61 |  | 336.31 | 336.03 | 335.7 | 335.44 | 335.26 | 335.26 | 335.26 | 335.27 | 335.21 | 335.15 |  | 335.09 |  | 334.81 |  | 334.59 |  | 334.59 | 334.58 | 334.58
CHM | 883.5 | 884.3 | 884.9 | 885.2 | 886.1 | 886.7 |  | 886.9 |  | 886.8 |  | 886.7 | 886.7 | 887.2 | 887.5 | 887 | 886.4 | 885.6 | 885.4 | 885.3 | 884.9 |  | 885.4 |  | 885.4 |  | 884.6 |  | 884.5 | 885.1 | 885.7
KL 1 | 0.33333: 1519.52; 0.54167: 1519.53
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1698.49; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/16)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 17
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/17 |  |  | 2080/10/17 |  |  | Thursday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 645.9 | 632.1 | 638.5 | 648.4 | 635.6 | 622.1 | 523.8 | 572.7 | 346.2 | 288.4 | 321.9 | 470.4 | 565.6 | 707 | 629.4 | 731 | 780.5 | 778.6 | 748.8 | 632.5 | 625 | 644.7 | 566 | 368.6 | 376.1 | 640.1 | 623.1 | 677.3 | 686.6 | 687.9 | 621.7
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1733MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1215 | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1339.69 | 1284.99 | 1729.69 | 1618.69 | 1731.19 | 1688.19 | 1542.99 | 1529.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1543.99 | 1668.69 | 1780.15 | 1770.45 | 1750.59 | 1666.09 | 1640.09 | 1607.19 | 1393.49 | 1311.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1770.45 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1770.45 MW
Solu Khola Dudhkoshi(86) | 26.6 | 26 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.4 | 25.9 | 28.5 | 28.5 | 28.5 | 86 | 28.5 | 25.4
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 17
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11.1 | 11.1 | 54 | 11.1 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/17)
Likhu-IV(52.4) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12.5 | 12.5 | 52.4 | 15 | 12.5
Upper Marsyangdi "A"(50) | 27.9 | 28.2 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.9 | 28.9 | 50 | 28.9 | 27.9 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.8 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 17.3 | 17.3 | 45 | 17.3 | 15.8 |  | IPP | 470.35 | 468.65 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.65 | 471.75 | 474.15 | 474.15
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.4 | 35.5 | 35.6 | 35.6 | 35.6 | 35.6 | 65.6 | 386.5 | 316.5 | 156.5 | 56.5 | 81.5 | 111.5 | 86.6 | 51.6 | 86.6 | 112.6 | 112.6 | 146.6 | 346.6 | 91.1 | 85.6 | 105.2 | 35.2
Mistri Khola(42) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.3 | 7.3 | 42 | 7.3 | 7 |  | NEA ROR PROR | 105.54 | 105.24 | 78.34 | 78.34 | 89.04 | 123.84 | 226.64 | 318.04 | 330.84 | 247.14 | 238.94 | 243.48 | 256.74 | 219.14 | 217.14 | 196.24 | 193.74 | 190.14 | 158.44 | 336.3 | 216.24 | 172.54 | 127.54 | 114.54
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 621.7 | 645.9 | 632.1 | 638.5 | 648.4 | 635.6 | 523.8 | 346.2 | 321.9 | 470.4 | 565.6 | 707 | 629.4 | 731 | 780.5 | 778.6 | 748.8 | 632.5 | 644.7 | 368.6 | 640.1 | 677.3 | 686.6 | 687.9
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 250 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 250 | 250 | 200 | 0 | 0
Nyadi(30) | 7 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 7.8 | 7.8 | 30 | 7.8 | 6.9 |  | System_Load | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1284.99 | 1619.69 | 1688.19 | 1542.99 | 1529.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1668.69 | 1770.45 | 1666.09 | 1607.19 | 1393.49 | 1311.79
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.5 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 5.8 | 5.8 | 28 | 7.5 | 5.8 |  | National_Load | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1284.99 | 1618.69 | 1688.19 | 1542.99 | 1529.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1668.69 | 1770.45 | 1666.09 | 1607.19 | 1393.49 | 1311.79
Dordi(27) | 6.2 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 6.5 | 6.5 | 30 | 6.5 | 5.7
Upper Madi(25) | 9.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 9.2 | 9.2 | 25 | 9.2 | 8.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 7.4 | 7.4 | 25 | 7.4 | 6.9
Solu Khola(23.5) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 23.5 | 6.8 | 6.7
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.9 | 9.8 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.6 | 10.6 | 22 | 10.6 | 9.8
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 20.5 | 20.8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19.8 | 19.8 | 17.6 | 17.6 | 19.1 | 16.7 | 15.6 | 15.6 | 15.6 | 17.6 | 18.4 | 19.4 | 19 | 19.7 | 240 | 21 | 15.6
Total IPP | 470.35 | 468.65 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.95 | 468.65 | 469.15 | 471.75 | 474.15 | 474.15 | 1042.4 | 474.15 | 468.65
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 30 | 320 | 350 | 370 | 280 | 120 | 20 | 45 | 75 | 50 | 15 | 50 | 76 | 76 | 15 | 110 | 160 | 310 | 290 | 50 | 50 | 50 | 70 | 0 | 456 | 370 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.4 | 8.5 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 14.1 | 14.1 | 8.6 | 8.2 | 8.2 | 22.1 | 14.1 | 8.2
Total NEA SUBSIDIARIES | 35.4 | 35.5 | 35.6 | 35.6 | 35.6 | 35.6 | 50.6 | 65.6 | 355.6 | 386.5 | 406.5 | 316.5 | 156.5 | 56.5 | 81.5 | 111.5 | 86.6 | 51.6 | 86.6 | 112.6 | 112.6 | 51.6 | 146.6 | 196.6 | 346.6 | 326.6 | 91.1 | 91.1 | 85.6 | 105.2 | 35.2 | 538.1 | 406.5 | 35.2
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 31.4 | 66.2 | 131.5 | 111.1 | 111.1 | 114.6 | 61.5 | 61.5 | 61.3 | 61.3 | 60.6 | 60.6 | 61.3 | 61.3 | 61.3 | 30 | 30 | 123 | 141 | 141 | 59.7 | 60.7 | 30.4 | 0 | 0 | 144 | 141 | 0
Middle MRS(70) | 26.6 | 26.4 | 0 | 0 | 0 | 34.8 | 34.8 | 24.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.9 | 23.3 | 23.3 | 23.5 | 23.5 | 23.5 | 34.7 | 34.7 | 34.7 | 24.8 | 24.8 | 35 | 35 | 35 | 22.8 | 22.9 | 22.9 | 22.9 | 35 | 70 | 35 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 38.7 | 34 | 64.5 | 64.2 | 64.2 | 66.9 | 52.3 | 52.2 | 51.74 | 68.1 | 40 | 40 | 16.9 | 16.9 | 16.9 | 17 | 17 | 49.7 | 54 | 54 | 34.7 | 34.7 | 34.8 | 16.8 | 0 | 69 | 68.1 | 0
U Trisuli 3A(60) | 37.1 | 36.3 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 38.8 | 35 | 35 | 36.8 | 36.8 | 36.3 | 36.3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 33 | 37.3 | 39.1 | 60 | 39.1 | 33
CHM(30) | 0 | 0 | 0 | 0 | 10.7 | 10.7 | 14.8 | 23.3 | 23.3 | 28.6 | 28.6 | 28.2 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 28.4 | 23 | 23.1 | 14.5 | 10.5 | 10.7 | 0 | 30 | 28.6 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.3 | 5.2 | 11.1 | 14.6 | 18 | 18.7 | 18.4 | 16.4 | 8 | 5.5 | 1.9 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.7 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 2 | 2 | 2 | 2 | 2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 15 | 4 | 0
DEVI(14.1) | 9.5 | 10.3 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 9 | 9.5 | 14.1 | 10.3 | 9
MODI(14) | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.3 | 14 | 3.3 | 3.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5
Total ROR | 105.54 | 105.24 | 78.34 | 78.34 | 89.04 | 123.84 | 198.04 | 226.64 | 332.44 | 318.04 | 319.34 | 330.84 | 247.14 | 238.94 | 243.48 | 256.74 | 219.14 | 217.14 | 196.24 | 193.74 | 190.14 | 148.44 | 158.44 | 298.6 | 336.3 | 328.94 | 216.24 | 206.74 | 172.54 | 127.54 | 114.54 | 489.91 | 336.3 | 78.34
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 58 | 56.6 | 58.3 | 61.5 | 60.8 | 67.1 | 63.7 | 52.7 | 59.2 | 62.5 | 62.4 | 53.7 | 60.3 | 57.7 | 70 | 57.7 | 70 | 71.2 | 66.6 | 68.3 | 62 | 67 | 63.5 | 72 | 64.6 | 62.6 | 56.3 | 61.1 | 59 | 66.9 | 72.9 |  | 72.9 | 52.7
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 395 | 388.9 | 405.2 | 407.9 | 404.5 | 397.6 | 377 | 373.8 | 390.3 | 171.3 | 111.2 | 158 | 305 | 389.4 | 447 | 391 | 440 | 486.9 | 493.1 | 459 | 399 | 428 | 446 | 350 | 160 | 155 | 406.5 | 389 | 410.2 | 405.6 | 410.9 |  | 493.1 | 111.2
RAMNAGAR | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30.3 | 41.9 | 33.1 | 36.9 | 30 | 20.9 | 26.8 | 52 | 39 | 40.4 | 41.2 | 32.6 | 43.4 | 29.1 | 26 | 30 | 36 | 36 | 32.1 | 34.1 | 34 | 38 | 32.2 | 37.2 |  | 52 | 5
RAXAUL 132 | 100 | 130 | 103 | 106.2 | 114 | 106 | 108.2 | 0 | 20.4 | 22.6 | 23 | 27 | 31 | 32 | 72 | 67 | 108 | 108 | 108.2 | 106 | 73 | 48 | 46 | 42 | 42 | 64 | 80 | 76 | 106 | 114 | 100 |  | 130 | 0
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 63.7 | 65.4 | 60.6 | 57.9 | 64.1 | 59.9 | 68.2 | 67 | 60.9 | 56.7 | 54.9 | 53.2 | 53.2 | 59.7 | 66 | 74.7 | 72.6 | 73.2 | 78.1 | 72.1 | 69.4 | 56 | 59.2 | 66 | 66 | 62.4 | 63.2 | 63 | 64.1 | 67.9 | 66.9 |  | 78.1 | 53.2
Total IMPORT | 621.7 | 645.9 | 632.1 | 638.5 | 648.4 | 635.6 | 622.1 | 523.8 | 572.7 | 346.2 | 288.4 | 321.9 | 470.4 | 565.6 | 707 | 629.4 | 731 | 780.5 | 778.6 | 748.8 | 632.5 | 625 | 644.7 | 566 | 368.6 | 376.1 | 640.1 | 623.1 | 677.3 | 686.6 | 687.9 | 0 | 780.5 | 288.4
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1339.69 | 1284.99 | 1729.69 | 1519.69 | 1483.19 | 1438.19 | 1342.99 | 1329.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1293.99 | 1418.69 | 1530.15 | 1520.45 | 1500.59 | 1416.09 | 1390.09 | 1407.19 | 1393.49 | 1311.79 | 2231.81 | 1729.69 | 1214.99
Interruption/Tripping | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 250 | 250 | 200 | 200 | 0 | [6 empty] | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 200 |  |  |  | 250 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1339.69 | 1284.99 | 1729.69 | 1619.69 | 1733.19 | 1688.19 | 1542.99 | 1529.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1543.99 | 1668.69 | 1780.15 | 1770.45 | 1750.59 | 1666.09 | 1640.09 | 1607.19 | 1393.49 | 1311.79 | 1693.71 | 1780.15 | 1214.99
TOTAL NATIONAL LOAD (ACTUAL) | 1232.99 | 1255.29 | 1214.99 | 1221.39 | 1241.99 | 1263.99 | 1339.69 | 1284.99 | 1729.69 | 1618.69 | 1731.19 | 1688.19 | 1542.99 | 1529.99 | 1500.93 | 1466.59 | 1505.69 | 1518.19 | 1530.39 | 1524.09 | 1404.19 | 1543.99 | 1668.69 | 1780.15 | 1770.45 | 1750.59 | 1666.09 | 1640.09 | 1607.19 | 1393.49 | 1311.79 |  | 1780.15 | 1214.99
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0
NET IMPORT | 621.7 | 645.9 | 632.1 | 638.5 | 648.4 | 635.6 | 622.1 | 523.8 | 572.7 | 345.2 | 286.4 | 321.9 | 470.4 | 565.6 | 707 | 629.4 | 731 | 780.5 | 778.6 | 748.8 | 632.5 | 625 | 644.7 | 566 | 368.6 | 376.1 | 640.1 | 623.1 | 677.3 | 686.6 | 687.9 |  | 780.5 | 286.4
HZ | 49.92 | 50.02 | 50.04 | 50 | 49.94 | 50.02 | 50 | 49.98 | 50.13 | 49.96 | 50.04 | 50.153 | 50.027 | 50.051 | 50.04 | 49.991 | 49.963 | 50.054 | 49.99 | 50.081 | 49.97 | 50.024 | 49.957 |  | 49.906 | 49.99 | 50.047 | 50.053 | 50.031 | 50.02 | 50.02 |  | 50.153 | 49.906
HTD 132KV | 127.6 | 128.5 | 127.6 | 127.6 | 128.8 | 127.8 | 128.2 | 127.9 | 124.2 | 127.3 | 127.1 | 126.3 | 127 | 125.6 | 124.3 | 125.4 | 125.4 | 124.6 | 123.1 | 123 | 127.8 | 125.9 | 124.9 |  | 127.1 | 129 | 129 | 129.5 | 129.2 | 128.2 | 129.2 |  | 129.5 | 123
SUI 132KV | 132.1 | 133 | 132.1 | 132.1 | 133 | 132 | 132 | 131.6 | 127.8 | 129 | 128.1 | 127.8 | 128.7 | 128 | 127 | 128.4 | 128.4 | 127.7 | 126.8 | 127.2 | 131 | 128.6 | 127.5 |  | 129 | 131 | 131.1 | 131.9 | 131.9 | 131.7 | 133 |  | 133 | 126.8
DUBI 132KV | 128.7 | 127.1 | 130.5 | 130.5 | 129 | 129.6 | 129.6 | 127.5 | 121.4 | 129.6 | 128.5 | 128.2 | 127.5 | 128 | 126.6 | 127.1 | 128.8 | 127.1 | 124.7 | 125.9 | 127.3 | 127.9 | 126.1 |  | 128.3 | 131 | 133 | 132.3 | 131.2 | 128.7 | 128.1 |  | 133 | 121.4
ANAMANI 132KV | 131.5 | 129.9 | 132.7 | 132.7 | 131.2 | 132.1 | 132.1 | 128.2 | 123 | 128.7 | 127 | 126.2 | 125.5 | 126.6 | 125.8 | 127.4 | 129 | 127 | 124.2 | 124.3 | 126.3 | 126.5 | 123.9 |  | 128.3 | 131 | 134 | 133.6 | 132.9 | 132 | 131.6 |  | 134 | 123
KG-A 132KV | 131.1 | 130.6 | 130 | 130 | 131 | 130.5 | 130.5 | 135.7 | 132.5 | 134.7 | 134.5 | 133.5 | 133.6 | 133 | 130.5 | 134.6 | 133.5 | 130 | 132.9 | 131.4 | 135.9 | 133.3 | 132.4 |  | 134.8 | 137 | 135.5 | 136.2 | 135.8 | 133.8 | 132.7 |  | 137 | 130
KOHALPUR 132KV | 133.4 | 131.8 | 133.1 | 133.1 | 132.7 | 127 | 127 | 127.4 | 128.6 | 132.2 | 128.1 | 129 | 135 | 133.3 | 126.8 | 130.6 | 132.4 | 134.8 | 131.3 | 134.4 | 134.5 | 134 | 136.3 |  | 132.3 | 135 | 132.7 | 133.9 | 135.9 | 130.6 | 133.3 |  | 136.3 | 126.8
SUI 66KV | 66.5 | 66.9 | 66.6 | 66.6 | 67.1 | 66.5 | 66.5 | 66.5 | 64.3 | 64.6 | 64.2 | 64.1 | 64.6 | 64.2 | 63.6 | 64.4 | 64.3 | 63.9 | 63.9 | 64.2 | 66 | 64.6 | 64 |  | 64.7 | 66 | 65.6 | 66 | 66.1 | 66.2 | 67.1 |  | 67.1 | 63.6
[33 empty] | 0 | 0
Kathmandu Load | 150.5 | 138.18 | 128.08 | 131.5 | 139.92 | 162 | 198.06 | 242.92 | 338.98 | 344.84 | 372.64 | 376.096 | 346.278 | 336.046 | 42 | 304.691 | 296.646 | 289.44 | 289.74 | 270.88 | 275.84 | 305.14 | 347.19 | 93.5 | 420.1 | 391.84 | 354.376 | 339.784 | 321.4 | 235.12 | 186.84 |  | 420.1 | 42
MRS-SYU | -6.9 | -10.6 | -18.1 | -15.9 | -14.9 | -7.6 | 6 | 18 | 40 | 38.9 | 37.1 | 40.4 | 31.1 | 26.9 | 26 | 27.6 | 16 | 18.5 | 13.2 | 8.5 | 16.4 | 10.5 | 10.3 |  | 40.8 | 46.1 | 24.5 | 24.2 | 19.6 | 4.8 | 1.3 | 75 | 46.1 | -18.1
NMRS-MATA | -12.6 | -16.2 | -25.7 | -26.2 | -24.3 | -12.9 | 2.9 | 18.2 | 52.9 | 52 | 49.3 | 53.9 | 42.9 | 36.4 | 29 | 30.4 | 15.5 | 18.7 | 12.4 | 6.9 | 20.8 | 15.2 | 15.25 |  | 54.6 | 62.4 | 33.7 | 32.2 | 20.5 | 1.6 | 0.8 | 240 | 62.4 | -26.2
KL2-MATA | -9.3 | -12.3 | -9.3 | -9.5 | -6 | -4 | 0 | 14 | 20 | 19 | 38 | 35 | 34 | 31 | 27 | 12 | 18.7 | 18 | 21.8 | 15 | 22 | 40 | 51 |  | 61 | 49 | 55.6 | 50.9 | 44.9 | 11.7 | -3.1 | 240 | 61 | -12.3
KL1-SYU | -6.2 | -7.8 | -9.8 | -8.2 | -7.3 | -7.2 | -3.9 | 1.9 | 14.3 | 18 | 22 | 22.6 | 21 | 20.3 | 6.3 | 1.5 | 3.2 | 0 | 2.4 | 5 | 12.6 | 19 | 23 |  | 31 | 29 | 26.7 | 25.2 | 17.8 | 2.7 | -3.5 | 60 | 31 | -9.8
KHIMTI-LAMOSANGHU | 96.96 | 96.64 | 103.04 | 103.36 | 104.48 | 105.76 | 105.12 | 102.88 | 123.84 | 128 | 136 | 128.256 | 119.238 | 119.906 | 115 | 125.751 | 136.606 | 129.6 | 145 | 143.04 | 115.2 | 132.8 | 160 |  | 139.2 | 118.4 | 126.936 | 122.344 | 133.66 | 125.28 | 100 | 120 | 160 | 96.64
LAMOSHANGU-BHAKTAPUR | 71.8 | 72.4 | 76.2 | 74.5 | 73.7 | 76 | 74.4 | 72.8 | 86.5 | 85.8 | 89.4 | 84.8 | 79.8 | 80 | 86 | 82.5 | 87.7 | 87 | 92.5 | 95 | 80 | 90 | 104 |  | 92 | 81 | 83.3 | 82.2 | 89.1 | 87.5 | 73.3
BALAJU-SYUCHATAR | 52 | 57.7 | 59.6 | 91.6 | 58.7 | 46.6 | 23.7 | 6.6 | 7.4 | -18.8 | -26.9 | -31.7 | -20.4 | -9.9 | 7.4 | 8.7 | 24.1 | 21.6 | 32.4 | 58.1 | 28 | 7 | 6 |  | -41 | -46 | -22.8 | -18.7 | 2.3 | 39.4 | 39.1
DHALKE-NAWALPUR I | 76.9 | 77 | 85.1 | 85.1 | 81 | 80.1 | 82.4 | 64.8 | 94.5 | 79.6 | 73.3 | 68.5 | 77.6 | 80.5 | 90 | 81 | 90.9 | 96.3 | 98.6 | 102 | 74 | 87 | 96.4 |  | 66 | 53 | 74 | 75.7 | 83.9 | 89.5 | 74.7 |  | 102 | 53
N. BHARATPUR-BARDGHAT I | 24.9 | 29.4 | 30.5 | 30.9 | 29.6 | 28 | 23.2 | -1.1 | -6.52 | -10.5 | -10.2 | -11.2 | -2.8 | 0 | -1.2 | -1.5 | 4.2 | 0 | 2.4 | 5.4 | 2.5 | 8 | 10 |  | -12 | -18 | 2.5 | 2.2 | 12.3 | 18 | 19.4 |  | 30.9 | -18
DAMAK-DUHABI | -9.6 | -7.9 | -7.7 | -7.1 | -7.3 | -10.8 | -16.8 | -27.6 | -34.9 | -44.1 | -48.3 | -46.1 | -28.4 | -32.1 | -28 | -24.7 | -23.1 | -25 | -28.8 | -37 | -40 | -44 | -52 |  | -46.5 | -42.1 | -33.9 | -31.5 | -25.9 | -18.5 | -13.6 |  | -7.1 | -52
HETAUDA-KAMANE | -20.7 | -22.7 | -27.3 | -24.1 | -28.4 | -25.7 | -17.36 | -17.7 | 0 | -9.8 | -18.3 | -15.6 | -20.5 | -21.8 | -34 | -17.5 | -27.1 | -27.2 | -34.3 | -31 | -32 | -41 | -50 |  | -28 | -20 | -40.8 | -40.7 | -43.4 | 32.6 | -22.2 |  | 32.6 | -50
MIRCHAIYA LAHAN 2 | 92.2 | 95.8 | 90.4 | 88.6 | 92.2 | 91.6 | 93.3 | 97.6 | 106.5 | 100.2 | 99.6 | 95.3 | 96.6 | 81.1 | 110 | 106 | 103.9 | 106.5 | 115.2 | 113 | 103.1 | 100 | 109 |  | 98 | 103 | 93.7 | 93.7 | 94.6 | 109.1 | 100.9 |  | 115.2 | 81.1
Water Level
UTK | 1983.89 | 1984.15 | 1984.4 | 1984.58 | 1984.8 | 1985 |  | 1985.2 |  | 1985.1 | 1984.72 | 1984.3 | 1983.7 | 1983.8 | 1983.9 | 1983.92 | 1983.89 | 1984.05 | 1984.15 | 1984.17 | 1984.12 |  | 1984.2 |  | 1984.03 |  | 1983.3 |  | 1983.38 | 1983.41 | 1983.5
KGA | 520.24 | 520.6 | 520.91 | 521.25 | 521.6 | 521.88 |  | 521.96 |  | 521.64 | 521.4 | 521.18 | 520.92 | 520.78 | 520.72 | 520.64 | 520.51 | 520.44 | 520.38 | 520.31 | 520.25 |  | 520.32 |  | 520 |  | 519.27 |  | 519.31 | 519.55 | 519.96
MMRS |  |  | 622.25 | 623.1 | 623.26 | 623.32 |  | 623.26 |  | 623.22 | 623.16 | 623.09 | 623.03 | 623.01 | 623.3 | 623.11 | 623.15 | 623.15 | 623.02 | 622.9 | 622.71 |  | 622.72 |  | 622.56 |  | 622.5 |  | 622.55 | 622.57 | 622.55
MRS | 334.79 | 335.1 | 335.5 | 335.83 | 336.16 | 336.51 |  | 336.57 |  | 336.41 | 336.22 | 336.1 | 335.71 | 335.38 | 335.99 | 334.59 | 334.25 | 334.2 | 334.3 | 334.53 | 334.68 |  | 334.8 |  | 334.77 |  | 334.51 |  | 334.47 | 334.51 | 334.84
CHM |  | 886.7 | 887.2 | 887.6 | 887.8 |  |  | 887.5 |  | 886.7 | 886.1 | 885.6 | 884.4 | 884.2 | 884.2 | 884 | 883.9 | 884.6 | 885.2 | 885.6 | 886.2 |  | 886.7 |  | 886.3 |  | 884.7 |  | 884.4 | 884.3 | 884.2
KL 1 | 0: 1519.55; 0.33333: 1519.56; 0.54167: 1519.57
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1733.19; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/17)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
[12 empty] | 438 | 425 | 409.4 | 492 | 466 | 490 | 501.9 | 543.1 | 535 | 475 | 443 | 556 | 510 | 470 | 445 | 456.5 | 439 | 460.2 | 475.6 | 410.9
Note on A2: Load Supply Group

## 18
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/18 |  |  | 2080/10/18 |  |  | Friday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 634.1 | 599.9 | 591 | 590 | 609 | 629.6 | 471 | 616 | 340.5 | 242.7 | 236.8 | 309 | 520.7 | 655.9 | 689.3 | 784.4 | 778.3 | 837.8 | 848.6 | 583.9 | 614.7 | 595.5 | 630.5 | 585.6 | 591.6 | 608.44 | 624.44 | 676 | 687.5 | 683 | 649
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1683MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1210 | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1339.19 | 1249.69 | 1468.89 | 1615.49 | 1669.49 | 1682.99 | 1591.99 | 1503.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1496.79 | 1583.39 | 1686.79 | 1834.15 | 1817.05 | 1723.29 | 1635.63 | 1556.83 | 1609.39 | 1342.39 | 1303.89
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1817.05 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1817.05 MW
Solu Khola Dudhkoshi(86) | 26.7 | 26.7 | 26.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 86 | 26.7 | 25.7
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 18
Super Dordi (54) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 0 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 54 | 10.5 | 0 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/18)
Likhu-IV(52.4) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 52.4 | 14.5 | 14.5
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 50 | 28.7 | 28.7 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75 | 0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833
Upper Bhotekoshi Khola(45) | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 45 | 15.9 | 15.9 |  | IPP | 473.75 | 473.75 | 473.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 430.55 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.2 | 35.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 276.2 | 441.2 | 301.2 | 51.2 | 106.2 | 112.2 | 112.2 | 36.3 | 36.2 | 85.3 | 95.3 | 135.3 | 188.2 | 93.1 | 63.1 | 43.1 | 43.1
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7.5 |  | NEA ROR PROR | 102.34 | 114.54 | 111.14 | 111.14 | 111.14 | 132.04 | 269.74 | 326.04 | 282.24 | 259.04 | 228.44 | 225.74 | 239.84 | 239.84 | 208.64 | 182.24 | 179.24 | 144.84 | 203.24 | 280.5 | 211.34 | 176.54 | 139.04 | 106.04
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 649 | 634.1 | 599.9 | 591 | 590 | 609 | 471 | 340.5 | 236.8 | 309 | 520.7 | 655.9 | 689.3 | 784.4 | 778.3 | 837.8 | 848.6 | 583.9 | 595.5 | 585.6 | 608.44 | 676 | 687.5 | 683
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 250 | 250 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 280 | 290 | 250 | 221 | 0 | 0
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 0 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 0 |  | System_Load | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1249.69 | 1615.49 | 1682.99 | 1591.99 | 1503.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1496.79 | 1686.79 | 1817.05 | 1635.63 | 1609.39 | 1342.39 | 1304.89
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 7.2 | 7.2 |  | National_Load | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1249.69 | 1615.49 | 1682.99 | 1591.99 | 1503.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1496.79 | 1686.79 | 1817.05 | 1635.63 | 1609.39 | 1342.39 | 1303.89
Dordi(27) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 30 | 6.5 | 0
Upper Madi(25) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 25 | 9.2 | 9.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 0
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 0 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 25 | 7.4 | 0
Solu Khola(23.5) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 23.5 | 6.7 | 6.7
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 22 | 10.6 | 10.6
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 0
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 21 | 21.2 | 21.2 | 19.8 | 19.8 | 20.8 | 20.8 | 19.2 | 20 | 20 | 20.1 | 18.6 | 18.6 | 18.6 | 18.6 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 240 | 21.9 | 18.6
Total IPP | 473.75 | 473.75 | 473.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 430.55 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 1042.4 | 473.75 | 430.55
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 240 | 340 | 405 | 265 | 15 | 70 | 76 | 76 | 0 | 0 | 50 | 60 | 80 | 100 | 140 | 145 | 90 | 50 | 20 | 20 | 0 | 0 | 456 | 405 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.2 | 8.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.3 | 9.2 | 8.3 | 8.3 | 8.3 | 8.3 | 16.1 | 16.2 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 22.1 | 16.2 | 8.2
Total NEA SUBSIDIARIES | 35.2 | 35.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 66.2 | 276.2 | 376.2 | 441.2 | 301.2 | 51.2 | 106.2 | 112.2 | 112.2 | 36.3 | 36.2 | 85.3 | 95.3 | 115.3 | 135.3 | 183.1 | 188.2 | 133.1 | 93.1 | 63.1 | 63.1 | 43.1 | 43.1 | 538.1 | 441.2 | 35.2
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 49.1 | 90 | 120 | 132.7 | 121.7 | 101.7 | 91 | 60 | 70 | 61 | 61 | 40.8 | 41 | 40.9 | 30 | 30.9 | 62.7 | 101.1 | 101.4 | 92.4 | 92.4 | 60 | 60 | 0 | 0 | 144 | 132.7 | 0
Middle MRS(70) | 22.8 | 35 | 35 | 35 | 35 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 25.1 | 25 | 24.8 | 40 | 25 | 25 | 22.8 | 24.7 | 24.9 | 22 | 23.9 | 23.8 | 34.8 | 34.7 | 21.9 | 0 | 0 | 0 | 22.5 | 22.5 | 70 | 40 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 22 | 41.8 | 60 | 69.2 | 68.6 | 69.3 | 51.4 | 52 | 52.9 | 25 | 45.7 | 45.7 | 32.8 | 31.8 | 32.3 | 15.8 | 0 | 32.8 | 44.3 | 44.2 | 35.4 | 35.4 | 33 | 33 | 33 | 0 | 69 | 69.3 | 0
U Trisuli 3A(60) | 39.1 | 39.1 | 36.3 | 36.3 | 36.3 | 35.3 | 35 | 35 | 35 | 35 | 37.1 | 36.8 | 36.8 | 36.3 | 36.3 | 36.3 | 36.3 | 36 | 35.8 | 36 | 35.8 | 35.5 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 60 | 39.1 | 33.7
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 15 | 23 | 23 | 10 | 10.2 | 10.2 | 15 | 15 | 22.7 | 0 | 0 | 0 | 0 | 10.4 | 14.1 | 24.7 | 22.6 | 10 | 10 | 10 | 10 | 10 | 30 | 24.7 | 0
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4.4 | 4.4 | 4.4 | 4.4 | 17 | 17 | 13.7 | 9.1 | 5.3 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15
GDK(15) | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 15 | 2.6 | 2.6
DEVI(14.1) | 9.5 | 9.5 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 14.1 | 9.5 | 8.9
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 14 | 3.3 | 3.3
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5
Total ROR | 102.34 | 114.54 | 111.14 | 111.14 | 111.14 | 132.04 | 200.64 | 269.74 | 313.94 | 326.04 | 327.84 | 282.24 | 259.04 | 228.44 | 225.74 | 239.84 | 239.84 | 208.64 | 182.24 | 179.24 | 144.84 | 130.64 | 203.24 | 267.8 | 280.5 | 245.84 | 211.34 | 176.54 | 176.54 | 139.04 | 106.04 | 489.91 | 327.84 | 102.34
KL1(60) | [31 empty] | 60 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0
TANAKPUR | 63.5 | 68.9 | 73.2 | 71 | 62 | 67 | 67.6 | 70 | 59 | 54.7 | 51.7 | 46.4 | 48 | 53.4 | 55.9 | 59.8 | 63 | 54.3 | 61.7 | 72.7 | 59.6 | 67.3 | 58.7 | 73.3 | 66.7 | 63 | 68 | 66 | 67 | 66 | 65 |  | 73.3 | 46.4
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 390.5 | 380.2 | 418 | 410 | 420 | 430 | 446 | 401 | 410 | 170 | 84 | 88 | 150 | 365 | 405 | 411.7 | 510 | 508.9 | 550 | 541 | 381.2 | 403 | 390.1 | 402 | 369.6 | 380.4 | 386 | 400 | 408 | 390 | 382 |  | 550 | 84
RAMNAGAR | 2.7 | 3 | 2.7 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 4 | 1.3 | 34 | 37 | 49.4 | 41.6 | 48 | 57 | 33.1 | 32.9 | 30.7 | 34.4 | 36 | 35.6 | 34 | 34 | 34 | 58 | 52 |  | 58 | 1.3
RAXAUL 132 | 120 | 128 | 106 | 108 | 106 | 110 | 114 |  | 80 | 50 | 36 | 36.4 | 34 | 32 | 90 | 107.6 | 92 | 102 | 108 | 102 | 52 | 50 | 50 | 51 | 41 | 46 | 58 | 62 | 100 | 104 | 115 |  | 128 | 32
NANPARA(33kV) | [32 empty] | 0 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test
JALESHWOR(33kV) | [32 empty] | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2
SAMPATIYA 132 kV | 72.3 | 54 | 0 | [5 empty] | 67 | 65.8 | 69 | 64 | 73 | 69 | 71 | 73.2 | 70 | 71.5 | 70.1 | 75.9 | 58 | 61.5 | 66 | 69.8 | 72.3 | 66.6 | 62.44 | 62.44 | 67 | 69.5 | 69 |  | 75.9 | 0
Total IMPORT | 649 | 634.1 | 599.9 | 591 | 590 | 609 | 629.6 | 471 | 616 | 340.5 | 242.7 | 236.8 | 309 | 520.7 | 655.9 | 689.3 | 784.4 | 778.3 | 837.8 | 848.6 | 583.9 | 614.7 | 595.5 | 630.5 | 585.6 | 591.6 | 608.44 | 624.44 | 676 | 687.5 | 683 | 0 | 848.6 | 236.8
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0
TOTAL SYSTEM LOAD (ACTUAL) | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1339.19 | 1249.69 | 1468.89 | 1415.49 | 1419.49 | 1432.99 | 1341.99 | 1273.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1296.79 | 1333.39 | 1406.79 | 1554.15 | 1527.05 | 1443.29 | 1385.63 | 1336.83 | 1388.39 | 1342.39 | 1304.89 | 2231.81 | 1609.19 | 1210.09
Interruption/Tripping | 0.29167: 200; 0.3125: 250; 0.33333: 250; 0.375: 250; 0.41667: 230; 0.70833: 200; 0.72917: 250; 0.75: 280; 0.77083: 280; 0.79167: 290; 0.8125: 280; 0.83333: 250; 0.85417: 220; 0.875: 221; 0.91667: 0; 0.95833: 0 |  | 290 | 0
TOTAL SYSTEM LOAD (EXPECTED) | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1339.19 | 1249.69 | 1468.89 | 1615.49 | 1669.49 | 1682.99 | 1591.99 | 1503.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1496.79 | 1583.39 | 1686.79 | 1834.15 | 1817.05 | 1723.29 | 1635.63 | 1556.83 | 1609.39 | 1342.39 | 1304.89 | 1693.71 | 1834.15 | 1210.09
TOTAL NATIONAL LOAD (ACTUAL) | 1260.29 | 1257.59 | 1220.99 | 1211.09 | 1210.09 | 1249.99 | 1339.19 | 1249.69 | 1468.89 | 1615.49 | 1669.49 | 1682.99 | 1591.99 | 1503.09 | 1460.59 | 1514.09 | 1609.19 | 1495.99 | 1528.99 | 1543.69 | 1496.79 | 1583.39 | 1686.79 | 1834.15 | 1817.05 | 1723.29 | 1635.63 | 1556.83 | 1609.39 | 1342.39 | 1303.89 |  | 1834.15 | 1210.09
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 0
NET IMPORT | 649 | 634.1 | 599.9 | 591 | 590 | 609 | 629.6 | 471 | 616 | 340.5 | 242.7 | 236.8 | 309 | 520.7 | 655.9 | 689.3 | 784.4 | 778.3 | 837.8 | 848.6 | 583.9 | 614.7 | 595.5 | 630.5 | 585.6 | 591.6 | 608.44 | 624.44 | 676 | 687.5 | 682 |  | 848.6 | 236.8
HZ | 50.03 | 50.03 | 49.96 | 49.983 | 50.013 | 50.034 | 50.04 | 50.05 | 50.074 | 50.07 | 50.042 | 50.074 | 49.899 | 50.045 | 49.936 | 49.941 | 50.065 | 50.048 | 49.81 | 49.958 | 49.998 | 50.09 | 50.075 | 49.973 | 49.963 | 49.923 | 50.049 | 50.048 | 50.048 | 50.06 | 49.93 |  | 50.09 | 49.81
HTD 132KV | 128.3 | 128.3 | 127.7 | 129.3 | 128.9 | 128.9 | 129.3 | 128.2 | 128 | 128.4 | 126.2 | 125.2 | 126.3 | 126.6 | 125.4 | 124.1 | 123.7 | 123.8 | 121.7 | 121.9 | 129 | 127.1 | 126.9 | 125.9 | 127 | 128.7 | 129 | 129 | 129 | 129 | 129.3 |  | 129.3 | 121.7
SUI 132KV | 132.6 | 132.6 | 131.9 | 133.3 | 132.7 | 132.7 | 132.8 | 130.1 | 131.2 | 130.4 | 127.8 | 127.1 | 128.3 | 128.8 | 128.2 | 127.3 | 127.4 | 127.7 | 125.7 | 125.4 | 130.8 | 129.1 | 128.7 | 127.4 | 128.3 | 130.1 | 130.4 | 130.4 | 130.4 | 132 | 132.3 |  | 133.3 | 125.4
DUBI 132KV | 129.7 | 129.7 | 128.2 | 130.9 | 129.7 | 127.8 | 128.7 | 128.7 | 128.7 | 128.8 | 126.6 | 129.2 | 127 | 126.2 | 126.4 | 123.9 | 123.4 | 127.3 | 120.1 | 125.7 | 129 | 129.3 | 125.1 | 126.7 | 130.4 | 132.1 | 132 | 132 | 132 | 131 | 127 |  | 132.1 | 120.1
ANAMANI 132KV | 132.9 | 132.9 | 130.2 | 132.6 | 130.8 | 128.9 | 129 | 128.6 | 127 | 127.8 | 125.6 | 129.5 | 125.3 | 125.6 | 126.8 | 125.7 | 125 | 127.9 | 120.7 | 123.9 | 128.7 | 127.9 | 123.4 | 125.2 | 129.7 | 131.9 | 131.6 | 131.6 | 131.6 | 132 | 128.9 |  | 132.9 | 120.7
KG-A 132KV | 131.7 | 131.7 | 131.3 | 132.9 | 132.7 | 135.1 | 135 | 135 | 135 | 136.8 | 134.8 | 134.1 | 134 | 133.9 | 132.3 | 132.3 | 131.6 | 132.3 | 131.7 | 129.7 | 136.6 | 133.1 | 133.1 | 134.6 | 135 | 135.7 | 136.4 | 136.4 | 136.4 | 133.5 | 131.6 |  | 136.8 | 129.7
KOHALPUR 132KV | 136.5 | 136.5 | 132.2 | 135 | 131 | 128.3 | 128.9 | 128.9 | 128.9 | 131.5 | 127.7 | 128.5 | 126.1 | 129.8 | 127.4 | 129 | 129.3 | 130.1 | 133.6 | 134 | 133.5 | 132.5 | 133.1 | 131.6 | 130.1 | 132.6 | 136 | 136 | 136 | 135 | 132.8 |  | 136.5 | 126.1
SUI 66KV | 66.8 | 66.8 | 66.8 | 67.2 | 67 | 67 | 66.9 | 66.9 | 66.9 | 65.4 | 63.9 | 63.8 | 64.9 | 65 | 64.5 | 64 | 63.9 | 64.3 | 63.2 | 62.8 | 65.6 | 64.8 | 64.5 | 63.8 | 64.4 | 65.4 | 65.2 | 65.2 | 65.2 | 66.4 | 66.5 |  | 67.2 | 62.8
[33 empty] | 0 | 0
Kathmandu Load | 154.52 | 142.74 | 136.66 | 137.14 | 144.333 | 198.52 | 199.8 | 241.62 | 346.64 | 342.76 | 372.74 | 375.543 | 374.84 | 315.84 | 42 | 311.824 | 292.92 | 297.902 | 300.109 | 306.2 | 305.587 | 317.266 | 363.881 | 414.147 | 414.234 | 382.583 | 344.34 | 330.34 | 330.34 | 217.34 | 167.74 |  | 414.234 | 42
MRS-SYU | -9.2 | -12.5 | -17.1 | -18.3 | -18.8 | 0 | -2.1 | 18 | 45 | 41.2 | 36.7 | 34.1 | 32 | 33.1 | 26.9 | 22.4 | 15.6 | 17.3 | 15.5 | 7.3 | 7.3 | 5.7 | 19.6 | 31.9 | 35.1 | 31 | 25 | 24 | 24 | 17 | 4.7 | 75 | 45 | -18.8
NMRS-MATA | -15.9 | -18.2 | -25 | -26.3 | -27.5 | -4.7 | -4.9 | 18.2 | 52 | 55.3 | 48.1 | 25.2 | 44 | 45 | 30.7 | 25.9 | 15.2 | 17.3 | 14.5 | 0.4 | 10.5 | 9.6 | 26.5 | 43.2 | 47 | 42.2 | 33 | 33 | 33 | 16 | 2.7 | 240 | 55.3 | -27.5
KL2-MATA | -9 | -11.1 | -11.4 | -11 | -7 | -1.2 | 0 | 14 | 24 | 27.1 | 35.8 | 41.7 | 28 | 29 | 24 | 15 | 12 | 12 | 16.5 | 27 | 38 | 45 | 52 | 60 | 59 | 56 | 53 | 47 | 47 | 6 | -4 | 240 | 60 | -11.4
KL1-SYU | -8 | -8.8 | -10.9 | -10 | -10.1 | -0.6 | -1.2 | 1.9 | 14 | 21 | 22 | 21.8 | 18 | 18 | 5 | 2.1 | 2.5 | 2 | 5.6 | 12 | 20.5 | 22.7 | 26.3 | 29.9 | 30.5 | 29.6 | 28 | 26 | 26 | 3 | -1 | 60 | 30.5 | -10.9
KHIMTI-LAMOSANGHU | 105.28 | 102 | 113.12 | 114.8 | 119.793 | 118.08 | 121.36 | 102.88 | 125 | 111.52 | 139.4 | 159.903 | 160 | 98.4 | 126.28 | 141.484 | 142.68 | 147.962 | 151.469 | 180.36 | 140.447 | 146.626 | 154.141 | 157.147 | 150.634 | 138.443 | 120 | 115 | 115 | 90 | 80 | 120 | 180.36 | 80
LAMOSHANGU-BHAKTAPUR | 78.9 | 76 | 80.7 | 80.1 | 82.1 | 81.5 | 82 | 72.8 | 86.5 | 76.6 | 90.6 | 101.5 | 84 | 78 | 83.7 | 91.7 | 92 | 93.1 | 94.7 | 101.9 | 87.5 | 93.4 | 94.3 | 98.1 | 93.9 | 88.8 | 85 | 81 | 81 | 72 | 69
BALAJU-SYUCHATAR | 59.2 | 57.7 | 65.9 | 67.9 | 68 | 47 | 46.7 | 6.6 | 7.4 | -35.7 | -24.8 | -6.8 | -22 | -24 | 4 | 17.6 | 38 | 38.7 | 37.7 | 48.7 | 20.1 | 20.5 | -2.1 | -15.2 | -21.2 | -18.5 | -11 | -11 | -11 | 22 | 37
DHALKE-NAWALPUR I | 79.1 | 83.1 | 90.4 | 86.6 | 92.5 | 85.2 | 91.6 | 64.8 | 94.5 | 57.2 | 70.5 | 87.4 | 67 | 67 | 87 | 86.5 | 86 | 91.2 | 93.3 | 100.5 | 93.3 | 95 | 90.5 | 93.4 | 91.5 | 81.9 | 81 | 81 | 81 | 75 | 73 |  | 100.5 | 57.2
N. BHARATPUR-BARDGHAT I | 32.1 | 36 | 43.5 | 45.9 | 44.8 | 36.1 | 37.3 | -1.1 | -6.52 | -10.5 | -5.1 | -3 | -6.5 | -8.1 | -1.6 | 3.2 | 2.4 | 2.9 | 4.2 | 10.9 | 7.1 | 3.7 | -5.2 | -10.9 | -10.8 | -10.4 | -7 | -7 | -7 | 6 | 7.5 |  | 45.9 | -10.9
DAMAK-DUHABI | -9.8 | -7.9 | -6.5 | -9.5 | -8.6 | -17.2 | -18 | -27.6 | -34.9 | -41.7 | -44 | -37.3 | -38 | -31 | -26 | -17.8 | -25 | -26.7 | -27.8 | -29.7 | -38.4 | -46.1 | -57 | -55.4 | -49.5 | -42.4 | -35 | -35 | -35 | -16 | -11.5 |  | -6.5 | -57
HETAUDA-KAMANE | -29 | -22.7 | -29.9 | -32.1 | -31.2 | -26.7 | -28 | -17.7 | 0 | -11 | -22.6 | -33.3 | -16 | -18 | 29 | 26.8 | 26 | 26 | 26.2 | 25.9 | -44 | -47.5 | -39.7 | -41.1 | -39.1 | -36 | -37 | -37 | -37 | 18 | -13.5 |  | 29 | -47.5
MIRCHAIYA LAHAN 2 | 95.8 | 95.4 | 92.1 | 89.5 | 91 | 96.7 | 93.1 | 97.6 | 106.5 | 96.3 | 96.3 | 96.7 | 95 | 98 | 112 | 107.7 | 114 | 119.1 | 127.4 | 116.4 | 94.1 | 100.2 | 116.4 | 118.5 | 111.8 | 103 | 95 | 95 | 95 | 97.5 | 99 |  | 127.4 | 89.5
Water Level
UTK | 1983.79 | 1984 | 1984.28 | 1984.49 | 1984.7 | 1984.92 |  | 1985.14 |  | 1985.12 |  | 1984.42 | 1983.3 | 1982.86 | 1983.1 | 1983.2 | 1983.2 | 1983.4 | 1983.63 | 1983.75 | 1983.62 |  | 1983.6 |  | 1983.45 |  | 1983.3 |  | 1983.5 | 1983.65 | 1983.9
KGA | 520.33 | 520.68 | 521 | 521.32 | 521.65 | 521.95 |  | 521.98 |  | 521.64 |  | 521.15 | 520.88 | 520.64 | 520.58 | 520 | 520.44 | 520.5 | 520.58 | 520.67 | 520.76 |  | 520.88 |  | 520.64 |  | 520.35 |  |  | 520.34 | 520.68
MMRS | 622.5 | 622.45 | 622.35 |  | 622.12 | 621.99 |  | 621.74 |  | 621.74 |  | 621.62 | 621.56 | 621.84 | 621.89 | 621.95 | 621.89 | 621.96 | 621.9 | 621.85 | 621.66 |  | 621.61 |  | 621.47 |  | 621.85 |  | 622.4
MRS | 335.15 | 335.48 | 335.83 | 336.1 | 336.35 | 336.55 |  | 336.58 |  | 336.34 |  | 336.01 | 335.86 | 335.7 |  | 335.55 | 335.51 | 335.49 | 335.46 | 335.42 | 335.32 |  | 335.54 |  | 335.51 |  | 335.46 |  | 335.43 | 335.41
CHM | 885.3 | 885.4 | 886 | 886.6 | 887.1 | 887.4 |  |  |  | 887.4 |  |  | 886.1 | 886.1 | 885.9 | 885.8 | 885 | 883.9 | 883 | 883.7 | 884.4 |  | 885 |  | 884.7 |  | 883.7 |  |  |  | 883.2
KL 1 | 0: 1519.58; 0.58333: 1519.61; 0.79167: 1519.61
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1682.99; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/18)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 19
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/19 |  |  | 2080/10/19 |  |  | Saturday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 603.4 | 602.4 | 577 | 603.8 | 606.7 | 601.9 | 584.7 | 615.6 | 347.9 | 165.2 | 168.1 | 261.1 | 472.9 | 547 | 609 | 570.4 | 610.6 | 586 | 569.6 | 535.1 | 548.8 | 534.9 | 413.4 | 289.9 | 317 | 490.6 | 484.7 | 584 | 587.5 | 578.4 | 620
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1583MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1161 | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1271.19 | 1313.99 | 1389.39 | 1316.79 | 1332.89 | 1582.99 | 1554.99 | 1441.59 | 1416.99 | 1331.49 | 1260.89 | 1310.29 | 1334.09 | 1334.49 | 1280.29 | 1365.99 | 1520.69 | 1672.45 | 1684.95 | 1618.09 | 1540.19 | 1451.89 | 1396.19 | 1354.69 | 1199.39
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1582.99 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1582.99 MW
Solu Khola Dudhkoshi(86) | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 25.1 | 25.4 | 25.4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 86 | 27.8 | 24
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 19
Super Dordi (54) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 54 | 10.5 | 10.5 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/19)
Likhu-IV(52.4) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 52.4 | 14.5 | 14.5
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 25 | 25 | 25 | 25 | 25 | 25 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 50 | 28.7 | 25 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 45 | 15.9 | 15.9 |  | IPP | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 468.45 | 468.75 | 468.75 | 467.35
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 52.3 | 287.3 | 477.3 | 327.2 | 57.2 | 37.2
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 42 | 7.5 | 7.5 |  | NEA ROR PROR | 96.04 | 96.04 | 96.04 | 73.54 | 98.14 | 114.44 | 204.24 | 208.84 | 269.14 | 297.94 | 302.74 | 265.44
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 620 | 603.4 | 602.4 | 577 | 603.8 | 606.7 | 584.7 | 347.9 | 168.1 | 261.1 | 472.9 | 547
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 140 | 100
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 30 | 7.8 | 7.8 |  | System_Load | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1313.99 | 1316.79 | 1582.99 | 1554.99 | 1441.59 | 1416.99
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 28 | 7.2 | 7.2 |  | National_Load | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1313.99 | 1316.79 | 1582.99 | 1554.99 | 1441.59 | 1416.99
Dordi(27) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 30 | 6.5 | 6.5
Upper Madi(25) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 25 | 9.2 | 9.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 25 | 7.4 | 7.4
Solu Khola(23.5) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 23.5 | 6.7 | 6.7
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 22 | 10.6 | 10.6
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 21.9 | 21.9 | 21.9 | 21.1 | 20.8 | 20.7 | 20.7 | 19.8 | 19.8 | 19.8 | 19.8 | 18.5 | 19.8 | 20.8 | 22.8 | 23.3 | 23.3 | 22.5 | 22.5 | 17.5 | 16.8 | 16 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 240 | 23.3 | 15.8
Total IPP | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 472.75 | 468.45 | 468.75 | 468.75 | 467.35 | 467.35 | 467.35 | 471.05 | 471.05 | 471.05 | 471.05 | 471.05 | 471.05 | 471.05 | 471.05 | 471.05 | 474.85 | 474.85 | 474.85 | 474.85 | 474.85 | 1042.4 | 474.85 | 467.35
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 250 | 420 | 440 | 290 | 20 | 0 | 0 | 0 | 0 | 25 | 55 | 40 | 50 | 50 | 250 | 280 | 190 | 15 | 30 | 30 | 30 | 0 | 456 | 440 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 14.1 | 14.1 | 14.1 | 8.5 | 8.5 | 8.5 | 8.5 | 22.1 | 14.1 | 8.5
Total NEA SUBSIDIARIES | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 52.3 | 87.3 | 287.3 | 457.3 | 477.3 | 327.2 | 57.2 | 37.2 | 37.2 | 37.2 | 37.2 | 62.2 | 91.1 | 76.1 | 86.1 | 86.1 | 286.1 | 321.1 | 231.1 | 56.1 | 65.5 | 65.5 | 65.5 | 35.5 | 538.1 | 477.3 | 35.5
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 31.4 | 59 | 59 | 63.2 | 63.2 | 91.7 | 102.4 | 111.8 | 70 | 62 | 30 | 30.7 | 48.7 | 40.3 | 40.3 | 30.6 | 49.2 | 92 | 144 | 144 | 102 | 60.2 | 60.2 | 60.2 | 0 | 144 | 144 | 0
Middle MRS(70) | 22.5 | 22.5 | 22.5 | 0 | 24.6 | 24.6 | 24.6 | 24.6 | 34.1 | 25 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 26.3 | 26.3 | 24.5 | 34.7 | 34.8 | 34.8 | 24.8 | 24.8 | 24.8 | 34.8 | 34.8 | 25 | 25 | 25 | 25 | 25 | 70 | 34.8 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 16.3 | 15.6 | 33 | 33 | 33 | 51.4 | 51.9 | 70 | 55.5 | 60 | 34 | 34 | 34.7 | 34.7 | 35.2 | 35.2 | 18 | 18 | 36 | 68 | 68 | 51 | 51 | 51 | 51 | 0 | 69 | 70 | 0
U Trisuli 3A(60) | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 36 | 36 | 36 | 36 | 37.1 | 37.1 | 35.8 | 35.8 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 60 | 37.8 | 33.7
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 10 | 10 | 14.8 | 10.3 | 10 | 10.5 | 10.5 | 10.5 | 23 | 28 | 26 | 15 | 15 | 10 | 15 | 10 | 30 | 28 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 3.1 | 3.1 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.5 | 6.8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 9.8 | 0 | [14 empty] | Tanakpur | 64 | 64 | 62.8 | 53.3 | 62.9 | 67 | 58 | 55 | 56.6 | 62.5 | 65 | 51 | 54 | 66.8 | 55.8 | 58.5 | 54.2 | 64.7 | 66.9 | 60 | 55 | 68 | 61 | 66
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 15 | 2.6 | 2.6 | [14 empty] | Muz | 411 | 410 | 420 | 435.5 | 437 | 430 | 184 | 30.5 | 129 | 320 | 340 | 404 | 406 | 418.4 | 409 | 392 | 383 | 384 | 124 | 302 | 357 | 347 | 342 | 398
DEVI(14.1) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 14.1 | 8.9 | 8.9 | [14 empty] | Ram | 2 | 2.4 | 3.2 | 3 | 3.8 | 4.7 | 5.9 | 4.6 | 4.6 | 17 | 40 | 40 | 3.4 | 6 | 9.4 | 10.1 | 7.2 | 8.6 | 10 | 8 | 7 | 6.5 | 2.4 | 2.4
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 14 | 3.3 | 3.3 | [14 empty] | Rax | 126 | 126 | 91 | 112 | 103 | 83 | 55 | 43 | 40 | 40 | 54 | 64 | 64 | 82 | 62.6 | 57.6 | 50.6 | 42.4 | 52 | 48 | 100 | 100 | 110 | 104
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 30.9 | 33.4 | 48 | 50 | 43 | 37.4 | 49.2 | 51.4 | 40.1 | 35.2 | 37 | 72.6 | 65 | 66 | 63 | 49.6
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 64 | 64 | 62.8 | 53.3 | 62.9 | 67 | 58 | 55 | 56.6 | 62.5 | 65 | 51 | 54 | 66.8 | 55.8 | 58.5 | 54.2 | 64.7 | 66.9 | 60 | 55 | 68 | 61 | 66
Total ROR | 96.04 | 96.04 | 96.04 | 73.54 | 98.14 | 114.44 | 159.24 | 204.24 | 213.74 | 208.84 | 237.64 | 269.14 | 297.94 | 302.74 | 265.44 | 217.94 | 185.94 | 191.44 | 214.84 | 202.74 | 198.04 | 160.04 | 178.64 | 251.9 | 352.9 | 348.94 | 268.64 | 226.84 | 221.84 | 226.84 | 110.64 | 489.91 | 352.9 | 73.54 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [15 empty] | 411 | 410 | 420 | 435.5 | 437 | 430 | 184 | 30.5 | 129 | 320 | 340 | 404 | 406 | 418.4 | 409 | 392 | 383 | 384 | 124 | 302 | 357 | 347 | 342 | 398
KL2(32) | [31 empty] | 32 | 0 | 0 | [15 empty] | 2 | 2.4 | 3.2 | 3 | 3.8 | 4.7 | 5.9 | 4.6 | 4.6 | 17 | 40 | 40 | 3.4 | 6 | 9.4 | 10.1 | 7.2 | 8.6 | 10 | 8 | 7 | 6.5 | 2.4 | 2.4
KL3(14) | [31 empty] | 14 | 0 | 0 | [15 empty] | 126 | 126 | 91 | 112 | 103 | 83 | 55 | 43 | 40 | 40 | 54 | 64 | 64 | 82 | 62.6 | 57.6 | 50.6 | 42.4 | 52 | 48 | 100 | 100 | 110 | 104
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 30.9 | 33.4 | 48 | 50 | 43 | 37.4 | 49.2 | 51.4 | 40.1 | 35.2 | 37 | 72.6 | 65 | 66 | 63 | 49.6
TANAKPUR | 66 | 64 | 64 | 62.8 | 53.3 | 62.9 | 61.7 | 67 | 65 | 58 | 54.6 | 55 | 56.6 | 62.5 | 65 | 51 | 54 | 66.8 | 55.8 | 58.5 | 54.2 | 51.4 | 64.7 | 64.3 | 66.9 | 61 | 60 | 56.7 | 55 | 68 | 61 |  | 68 | 51
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 398 | 411 | 410 | 420 | 435.5 | 437 | 451 | 430 | 428 | 184 | 25 | 30.5 | 129 | 320 | 340 | 404 | 406 | 418.4 | 409 | 392 | 383 | 409 | 384 | 258 | 124 | 118 | 302 | 307 | 357 | 347 | 342 |  | 451 | 25
RAMNAGAR | 2.4 | 2.4 | 2.4 | 3.2 | 3 | 3.8 | 4.2 | 4.7 | 5.4 | 5.9 | 4.6 | 4.6 | 4.6 | 17 | 40 | 40 | 3.4 | 6 | 9.4 | 10.1 | 7.2 | 8 | 8.6 | 10.3 | 10 | 9 | 8 | 5 | 7 | 6.5 | 2.4 |  | 40 | 2.4 | [22 empty] | 64 | 0 | 411 | 2 | 126 | 0
RAXAUL 132 | 104 | 126 | 126 | 91 | 112 | 103 | 85 | 83 | 76 | 55 | 46 | 43 | 40 | 40 | 54 | 64 | 64 | 82 | 62.6 | 57.6 | 50.6 | 44.4 | 42.4 | 46.4 | 52 | 56.6 | 48 | 56 | 100 | 100 | 110 |  | 126 | 40 | [22 empty] | 64 | 0 | 410 | 2.4 | 126 | 0
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 62.8 | 0 | 420 | 3.2 | 91 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 53.3 | 0 | 435.5 | 3 | 112 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 62.9 | 0 | 437 | 3.8 | 103 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 67 | 0 | 430 | 4.7 | 83 | 0
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 58 | 0 | 184 | 5.9 | 55 | 45
SAMPATIYA 132 kV | 49.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.2 | 45 | 35 | 35 | 30.9 | 33.4 | 48 | 50 | 43 | 37.4 | 49.2 | 51.4 | 40.1 | 36 | 35.2 | 34.4 | 37 | 72.4 | 72.6 | 60 | 65 | 66 | 63 |  | 72.6 | 0 | [22 empty] | 55 | 0 | 30.5 | 4.6 | 43 | 35
Total IMPORT | 620 | 603.4 | 602.4 | 577 | 603.8 | 606.7 | 601.9 | 584.7 | 615.6 | 347.9 | 165.2 | 168.1 | 261.1 | 472.9 | 547 | 609 | 570.4 | 610.6 | 586 | 569.6 | 535.1 | 548.8 | 534.9 | 413.4 | 289.9 | 317 | 490.6 | 484.7 | 584 | 587.5 | 578.4 | 0 | 620 | 165.2 | [22 empty] | 56.6 | 0 | 129 | 4.6 | 40 | 30.9
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 62.5 | 0 | 320 | 17 | 40 | 33.4
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 65 | 0 | 340 | 40 | 54 | 48
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 51 | 0 | 404 | 40 | 64 | 50
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 54 | 0 | 406 | 3.4 | 64 | 43
TOTAL SYSTEM LOAD (ACTUAL) | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1271.19 | 1313.99 | 1389.39 | 1316.79 | 1332.89 | 1382.99 | 1354.99 | 1301.59 | 1316.99 | 1331.49 | 1260.89 | 1310.29 | 1334.09 | 1334.49 | 1280.29 | 1265.99 | 1270.69 | 1422.45 | 1434.95 | 1368.09 | 1290.19 | 1251.89 | 1346.19 | 1354.69 | 1199.39 | 2231.81 | 1434.95 | 1160.59 | [22 empty] | 66.8 | 0 | 418.4 | 6 | 82 | 37.4
Interruption/Tripping | 0.33333: 200; 0.375: 200; 0.41667: 140; 0.45833: 100; 0.72917: 100; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 200; 0.875: 50 |  | 250 | 50 | [22 empty] | 55.8 | 0 | 409 | 9.4 | 62.6 | 49.2
TOTAL SYSTEM LOAD (EXPECTED) | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1271.19 | 1313.99 | 1389.39 | 1316.79 | 1332.89 | 1582.99 | 1554.99 | 1441.59 | 1416.99 | 1331.49 | 1260.89 | 1310.29 | 1334.09 | 1334.49 | 1280.29 | 1365.99 | 1520.69 | 1672.45 | 1684.95 | 1618.09 | 1540.19 | 1451.89 | 1396.19 | 1354.69 | 1199.39 | 1693.71 | 1684.95 | 1160.59 | [22 empty] | 58.5 | 0 | 392 | 10.1 | 57.6 | 51.4
TOTAL NATIONAL LOAD (ACTUAL) | 1226.09 | 1209.49 | 1208.49 | 1160.59 | 1211.99 | 1231.19 | 1271.19 | 1313.99 | 1389.39 | 1316.79 | 1332.89 | 1582.99 | 1554.99 | 1441.59 | 1416.99 | 1331.49 | 1260.89 | 1310.29 | 1334.09 | 1334.49 | 1280.29 | 1365.99 | 1520.69 | 1672.45 | 1684.95 | 1618.09 | 1540.19 | 1451.89 | 1396.19 | 1354.69 | 1199.39 |  | 1684.95 | 1160.59 | [22 empty] | 54.2 | 0 | 383 | 7.2 | 50.6 | 40.1
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 64.7 | 0 | 384 | 8.6 | 42.4 | 35.2
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 66.9 | 0 | 124 | 10 | 52 | 37
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 60 | 0 | 302 | 8 | 48 | 72.6
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 55 | 0 | 357 | 7 | 100 | 65
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 68 | 0 | 347 | 6.5 | 100 | 66
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61 | 0 | 342 | 2.4 | 110 | 63
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 66 | 0 | 398 | 2.4 | 104 | 49.6
NET IMPORT | 620 | 603.4 | 602.4 | 577 | 603.8 | 606.7 | 601.9 | 584.7 | 615.6 | 347.9 | 165.2 | 168.1 | 261.1 | 472.9 | 547 | 609 | 570.4 | 610.6 | 586 | 569.6 | 535.1 | 548.8 | 534.9 | 413.4 | 289.9 | 317 | 490.6 | 484.7 | 584 | 587.5 | 578.4 |  | 620 | 165.2
HZ | 50.01 | 50.02 | 49.99 | 50.038 | 50.048 | 50.04 | 49.965 | 50.071 | 50.168 | 50.04 | 50.072 | 49.997 | 50.012 | 50.012 | 50.05 | 49.948 | 50.068 | 50.03 | 49.947 | 49.9763 | 49.944 | 49.964 | 49.954 | 49.927 | 49.973 | 50.009 | 50.027 | 49.989 | 49.991 | 50.104 | 49.941 |  | 50.168 | 49.927
HTD 132KV | 129.3 | 129 | 129 | 127.8 | 127.8 | 127.8 | 128.1 | 128.8 | 128 | 129 | 127.3 | 126.6 | 126.8 | 128.1 | 128.6 | 127.7 | 126.9 | 126.8 | 125.5 | 126.8 | 129.1 | 129 | 129 | 128.3 | 129.4 | 130.2 | 130.7 | 131.1 | 130.1 | 130.7 | 131 |  | 131.1 | 125.5
SUI 132KV | 131.6 | 132 | 132 | 131.2 | 131.4 | 131.4 | 131.2 | 131.2 | 130.6 | 130.4 | 128.9 | 128.2 | 128.2 | 129.5 | 130.7 | 130 | 129.7 | 129.9 | 128.7 | 129.6 | 131.6 | 131.1 | 131 | 129.8 | 130.8 | 131.3 | 132.1 | 132.8 | 132.6 | 133.5 | 133.9 |  | 133.9 | 128.2
DUBI 132KV | 128 | 130 | 130 | 127.8 | 128.7 | 128.7 | 129.2 | 130.9 | 125.2 | 129.5 | 127.8 | 128.7 | 131.1 | 127.5 | 126.6 | 127.7 | 128 | 126.5 | 125.8 | 125.8 | 129 | 128.2 | 127.9 | 126.8 | 131.4 | 130.7 | 128.5 | 126.9 | 128.3 | 129.3 | 130.5 |  | 131.4 | 125.2
ANAMANI 132KV | 130 | 131 | 131 | 130 | 131.1 | 131.1 | 130.6 | 132.8 | 128.7 | 129.3 | 127 | 130.2 | 132.5 | 128.5 | 128.2 | 128.6 | 128.8 | 128.4 | 126.8 | 127.1 | 129 | 126.4 | 126.1 | 125.2 | 131.5 | 131.5 | 128.7 | 127.2 | 129.5 | 130.5 | 131.9 |  | 132.8 | 125.2
KG-A 132KV | 130 | 132.8 | 132.8 | 130 | 130.6 | 130.6 | 132.6 | 133.8 | 135.9 | 134.1 | 134 | 134.5 | 134.1 | 135.2 | 135.2 | 132.5 | 130 | 131.4 | 132.3 | 132.5 | 135.1 | 135.7 | 135.3 | 135.4 | 135.5 | 136.2 | 136.2 | 136.4 | 133.1 | 132.6 | 132.2 |  | 136.4 | 130
KOHALPUR 132KV | 131 | 134 | 134 | 132.1 | 130 | 130 | 130.6 | 126.6 | 126..6 | 134.8 | 134 | 128.1 | 130.1 | 131.7 | 131.7 | 133.3 | 128.8 | 123.9 | 127.2 | 132.5 | 132.2 | 131.9 | 128.78 | 127.8 | 131.8 | 134.65 | 135.6 | 134.9 | 134.4 | 128.85 | 127 |  | 135.6 | 123.9
SUI 66KV | 66.2 | 66.7 | 66.7 | 66 | 66.1 | 66.1 | 66 | 65.9 | 65.6 | 65.3 | 65 | 64.1 | 63.9 | 64.9 | 64.9 | 65.3 | 64.9 | 65.1 | 64.5 | 65 | 66.1 | 65.7 | 65.7 | 65.1 | 65.7 | 65.9 | 66.2 | 66.6 | 66.6 | 67.2 | 67 |  | 67.2 | 63.9
[33 empty] | 0 | 0
Kathmandu Load | 141.54 | 112.34 | 105.34 | 127.84 | 132.84 | 132.84 | 186.34 | 221.84 | 250.64 | 282.34 | 325.04 | 345.016 | 343.708 | 334.46 | 42 | 292.28 | 247.44 | 237.091 | 258.04 | 254.571 | 250.94 | 288.24 | 307.74 | 362 | 366.4 | 351.94 | 312.46 | 297.743 | 248.84 | 202.04 | 156.3 |  | 366.4 | 42
MRS-SYU | -10 | -15 | -18 | -23.6 | -22.1 | -22.1 | -14.9 | -2.7 | 7.2 | 12 | 17 | 22.4 | 39.9 | 39.2 | 40 | 20.2 | 5.5 | 4 | 9.3 | 9.8 | 10.2 | 8 | 13 | 24 | 46 | 55 | 45 | 41.8 | 17.8 | 2.3 | -7.5 | 75 | 55 | -23.6
NMRS-MATA | -15.8 | -23 | -27 | -35.4 | -29.7 | -29.7 | -23 | -8 | 5.6 | 19.3 | 24 | 31.5 | 54.2 | 53.3 | 48 | 21.2 | 0.5 | -1.2 | 7.2 | 7.4 | 13.6 | 11.9 | 18 | 31 | 59 | 72.4 | 61 | 56.2 | 20.4 | 0.9 | -12.5 | 240 | 72.4 | -35.4
KL2-MATA | -2 | -8 | -8 | -7 | -10 | -10 | 8 | 10.1 | 17 | 23 | 30 | 32.8 | 23.9 | 28 | 28 | 20.3 | 9 | 4.2 | 10.6 | 16.5 | 19 | 39 | 44 | 47 | 34 | 30.4 | 26 | 23 | 15 | 5 | -3 | 240 | 47 | -10
KL1-SYU | -1 | -7 | -7 | -5.1 | -9.1 | -9.1 | 0.4 | 5 | 5 | 17 | 20 | 20.8 | 20.5 | 21.4 | 22.4 | 8.5 | 12 | 4.9 | 2.3 | 6.5 | 7.1 | 18.2 | 20 | 23 | 24 | 24.6 | 22.5 | 21 | 9.8 | 8 | 3.3 | 60 | 24.6 | -9.1
KHIMTI-LAMOSANGHU | 85 | 80 | 80 | 113.6 | 118.4 | 118.4 | 126.4 | 128 | 126.4 | 121.6 | 144 | 144.976 | 112.668 | 95.12 | 95.12 | 124.64 | 123 | 126.651 | 130.4 | 120.131 | 112 | 123.2 | 124.8 | 142.4 | 108.8 | 81.6 | 70.52 | 68.303 | 98.4 | 98.4 | 88.56 | 120 | 144.976 | 68.303
LAMOSHANGU-BHAKTAPUR | 74 | 77 | 77 | 81 | 83 | 83 | 86.3 | 87 | 86 | 84 | 95 | 93.5 | 77 | 68.2 | 68.2 | 82 | 81 | 85 | 88.4 | 82.4 | 79.4 | 84.2 | 84 | 93.4 | 77 | 56.4 | 58 | 56.5 | 72 | 72 | 69
BALAJU-SYUCHATAR | 59 | 64 | 64 | 77 | 75.1 | 75.1 | 65.3 | 52 | 34 | 14 | 12 | 4.5 | -25 | -27 | -27 | 19 | 51 | 53.8 | 34.4 | 24.8 | 16.4 | 2.4 | -3.4 | -12 | -43 | -63.6 | -50 | -44.5 | 8 | 30.9 | 45
DHALKE-NAWALPUR I | 80 | 88 | 88 | 96 | 94.1 | 94.1 | 100 | 101 | 89 | 74 | 79 | 77.9 | 51.3 | 45.4 | 45.4 | 72 | 77 | 76.7 | 79 | 85 | 74.5 | 80 | 79 | 78.1 | 56 | 39 | 44 | 46.4 | 65 | 70 | 73 |  | 101 | 39
N. BHARATPUR-BARDGHAT I | 28 | 36 | 36 | 39 | 45 | 45 | 38 | 28 | 15 | 11 | 12 | 2.9 | -10.6 | -10.2 | -10.2 | 0 | 18 | 16.9 | 12.7 | 12.2 | 18 | 6 | 2.4 | -7 | -16 | -25.3 | -21 | -13 | -1.7 | 10 | 21 |  | 45 | -25.3
DAMAK-DUHABI | -11 | -10 | -10 | -8 | -10 | -10 | -19 | -27.1 | -34 | -40 | -35 | -25.2 | -18 | -18.8 | -18.8 | -18.2 | -15 | -24.2 | -21.9 | -27.1 | -33.5 | -48.5 | -50 | -56 | -46.3 | -40.2 | -33 | -29 | -23 | -16 | -12 |  | -8 | -56
HETAUDA-KAMANE | -24 | -30 | -30 | -34 | -34 | -34 | -43.7 | -39 | -31 | -29 | -35 | -30.6 | 8.9 | 8.9 | 8.9 | 15.9 | 25 | 26.5 | 27.2 | -30.4 | -33.1 | -40.2 | -39.4 | -35 | -12 | 2.7 | -5.1 | -8.7 | -22 | -21 | -20 |  | 27.2 | -43.7
MIRCHAIYA LAHAN 2 | 92 | 85 | 85 | 91 | 88 | 88 | 87.4 | 95 | 100 | 92 | 83 | 79.4 | 75.2 | 93 | 93 | 99 | 93 | 98.9 | 95.8 | 94.8 | 103 | 90 | 95 | 111 | 103.1 | 94 | 93 | 103.3 | 101 | 90.7 | 83 |  | 111 | 75.2
Water Level
UTK | 1984.18 | 1984.42 | 1984.6 | 1984.87 | 1985.09 | 1985.3 |  | 1985.5 |  | 1985.5 |  | 1984.62 | 1983.48 | 1983.3 | 1983.45 | 1983.69 | 1983.9 | 1984.1 | 1984.3 | 1984.42 | 1984.49 |  | 1984.62 |  | 1984.28 |  | 1983.95 |  | 1984.15 | 1984.3 | 1984.5
KGA | 521.04 | 521.33 | 521.61 | 521.94 | 522.26 | 522.52 |  | 522.7 |  | 522.64 |  | 522.54 | 522.34 | 522.04 | 521.81 | 521.74 |  | 521.98 | 522.05 | 522.11 | 522.2 |  | 522.32 |  | 522.02 |  | 521.42 |  | 521.26 | 521.4 | 521.74
MMRS | 622.7 | 622.8 | 622.89 | 623.12 | 623.39 | 623.4 |  | 623.38 |  | 623.4 |  | 623.4 | 623.33 | 623.34 | 623.16 | 623.09 | 622.78 | 622.99 | 622.92 | 622.77 | 622.71 |  | 622.67 |  | 622.65 |  | 622.55 |  | 622.65 | 622.7 | 622.69
MRS | 335.8 | 336.18 | 336.35 | 336.57 | 336.7 | 336.81 |  | 336.89 |  | 336.85 |  | 336.75 | 336.54 | 336.25 | 335.95 | 335.64 | 335.6 | 335.6 | 335.59 | 335.57 | 335.58 |  | 335.62 |  | 335.53 |  | 335.75 |  | 334.91 | 335.02 | 335.37
CHM | 883.6 | 884.3 | 884.9 | 885.5 | 886.1 | 886.5 |  | 886.6 |  | 886.5 |  | 886.4 | 886.3 | 886 | 885.8 | 885.7 |  | 885.5 | 885.4 | 885.5 | 885.4 |  | 885.4 |  | 884.3 |  | 883.3 |  | 883.2 | 883.2 | 883.2
KL 1 | 0: 1519.62
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1582.99; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/19)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 20
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/20 |  |  | 2080/10/20 |  |  | Sunday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 600.5 | 498.9 | 475.1 | 490.8 | 536.6 | 565.8 | 540.1 | 551.7 | 358.4 | 178.5 | 126.5 | 224 | 481.1 | 556.5 | 559.3 | 632 | 716.3 | 712 | 613.8 | 654.7 | 612.7 | 542.1 | 497.4 | 445.8 | 479 | 520.5 | 531.5 | 604.1 | 522.7 | 529.9 | 547
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1586MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1098 | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1246.99 | 1275.29 | 1362.69 | 1397.19 | 1555.39 | 1586.09 | 1508.19 | 1415.59 | 1547.29 | 1470.09 | 1348.89 | 1459.09 | 1434.19 | 1395.79 | 1335.09 | 1443.09 | 1611.79 | 1716.59 | 1674.99 | 1581.29 | 1482.79 | 1442.29 | 1421.79 | 1248.79 | 1206.09
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1586.09 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1586.09 MW
Solu Khola Dudhkoshi(86) | 27.8 | 27.8 | 27.8 | 27.8 | 21.8 | 22.6 | 22.6 | 24.7 | 25 | 25 | 26.4 | 26.4 | 26.6 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 86 | 27.8 | 21.8
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 20
Super Dordi (54) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 54 | 10.5 | 10.5 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/20)
Likhu-IV(52.4) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 52.4 | 14.8 | 14.5
Upper Marsyangdi "A"(50) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 50 | 28.7 | 25.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 45 | 17.1 | 15.9 |  | IPP | 474.85 | 474.85 | 474.85 | 474.85 | 468.85 | 469.65 | 471.75 | 472.05 | 473.45 | 473.65 | 472.25 | 472.25
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 36.7 | 36.7 | 36.7 | 37.2 | 37.2 | 37.2 | 67.2 | 337.2 | 493.2 | 337.2 | 52.2 | 113.2
Mistri Khola(42) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 42 | 7.5 | 6.5 |  | NEA ROR PROR | 100.64 | 75.64 | 100.64 | 110.74 | 110.74 | 111.64 | 196.24 | 229.54 | 312.94 | 293.34 | 270.04 | 285.34
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 547 | 600.5 | 498.9 | 475.1 | 490.8 | 536.6 | 540.1 | 358.4 | 126.5 | 224 | 481.1 | 556.5
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 140 | 120
Nyadi(30) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 30 | 9.1 | 7.8 |  | System_Load | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1275.29 | 1397.19 | 1586.09 | 1508.19 | 1415.59 | 1547.29
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 28 | 7.3 | 7.2 |  | National_Load | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1275.29 | 1397.19 | 1586.09 | 1508.19 | 1415.59 | 1547.29
Dordi(27) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 30 | 8.7 | 6.5
Upper Madi(25) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 25 | 11.1 | 9.2
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 25 | 8.6 | 7.4
Solu Khola(23.5) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.7
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 22 | 19.8 | 10.6
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 20 | 20 | 20 | 20 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 17.7 | 20.1 | 19.3 | 21 | 21.8 | 21.8 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 18.1 | 17.8 | 17.8 | 17.8 | 17.8 | 240 | 21.8 | 17.7
Total IPP | 474.85 | 474.85 | 474.85 | 474.85 | 468.85 | 469.65 | 469.65 | 471.75 | 472.05 | 472.05 | 473.45 | 473.45 | 473.65 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 472.25 | 486.55 | 486.55 | 486.55 | 486.55 | 486.55 | 1042.4 | 486.55 | 468.85
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 300 | 400 | 456 | 300 | 15 | 76 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 90 | 110 | 120 | 120 | 75 | 20 | 0 | 456 | 456 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 9.7 | 9.7 | 9.7 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 16.1 | 16.1 | 16.1 | 16.2 | 9.5 | 9.5 | 9.5 | 9.5 | 22.1 | 16.2 | 9.5
Total NEA SUBSIDIARIES | 36.7 | 36.7 | 36.7 | 37.2 | 37.2 | 37.2 | 37.2 | 67.2 | 117.2 | 337.2 | 437.2 | 493.2 | 337.2 | 52.2 | 113.2 | 117.2 | 37.2 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 123.1 | 133.1 | 153.1 | 163.2 | 156.5 | 111.5 | 56.5 | 36.5 | 538.1 | 493.2 | 36.5
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 62 | 71.2 | 71.2 | 97.5 | 120 | 112 | 91.7 | 90 | 121.3 | 61.3 | 60.7 | 60.8 | 97.6 | 29.8 | 29.8 | 104 | 143.9 | 143.9 | 125.3 | 121 | 81.1 | 40.1 | 30.4 | 0 | 144 | 143.9 | 0
Middle MRS(70) | 25 | 0 | 25 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 70 | 35.8 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 21.6 | 22 | 33.5 | 45.3 | 64.3 | 64.3 | 52.6 | 52.6 | 68 | 68 | 50.3 | 50 | 16.7 | 44.6 | 18.3 | 18.3 | 64 | 68.5 | 68.5 | 62.5 | 52.4 | 35.2 | 52.3 | 33.3 | 34.3 | 69 | 68.5 | 0
U Trisuli 3A(60) | 35.8 | 35.8 | 35.8 | 36 | 36 | 37.3 | 39.3 | 38.8 | 38 | 40.1 | 39.8 | 39.8 | 36.8 | 36.8 | 36.8 | 40 | 40 | 38.3 | 39.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.1 | 52.5 | 41.3 | 43.3 | 42.8 | 60 | 52.5 | 35.8
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 15 | 10 | 10 | 15.1 | 9.8 | 10 | 15 | 15 | 10.1 | 10.1 | 10.1 | 28.8 | 28.8 | 26.5 | 23 | 22.9 | 9.9 | 0 | 0 | 30 | 28.8 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.9 | 3 | 5 | 6.6 | 3 | 3.5 | 1.9 | 8.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8.5 | 0 | [14 empty] | Tanakpur | 65 | 51 | 37.3 | 34.7 | 53 | 59.2 | 63.7 | 59.3 | 56.8 | 58.8 | 59.9 | 55 | -31.4 | 40.2 | 0 | 0 | 58.1 | 0 | 57.1 | 63.8 | 58.9 | 43.7 | 60.2 | 66
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 24 | 15 | 14 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2.6 | 2.6 | 2.6 | 2 | 2 | 2 | 2 | 2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 15 | 2.6 | 2 | [14 empty] | Muz | 370 | 375 | 385 | 398 | 435 | 411.2 | 200 | 7.6 | 113.2 | 364.3 | 410 | 412 | 457 | 480.8 | 503 | 449.3 | 469 | 422 | 284.5 | 287 | 360 | 334 | 410 | 320
DEVI(14.1) | 8.9 | 8.9 | 8.9 | 9.4 | 9.3 | 9 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 11 | 11 | 11 | 11 | 11 | 14.1 | 11 | 7.5 | [14 empty] | Ram | 3 | 3.1 | 3.8 | 3.1 | 3.8 | 9.3 | 39.5 | 20.9 | 18 | 20 | 40 | 43.2 | 45.7 | 41.8 | 51.9 | 28.2 | 23.8 | 21 | 17.7 | 39.2 | 45 | 2.8 | 17.1 | 3
MODI(14) | 3.3 | 3.3 | 3.3 | 3.5 | 3.6 | 3.5 | 3.6 | 3.6 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 14 | 3.6 | 3.3 | [14 empty] | Rax | 108 | 14 | 0 | 0 | 0 | 11 | 16.7 | 0 | 0 | 0 | 0 | 0 | 87 | 107.6 | 107.4 | 91.6 | 65.8 | 59.2 | 59 | 92 | 91 | 92 | 0 | 108
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 55 | 55.8 | 49 | 55 | 44.8 | 49.4 | 38.5 | 38.7 | 36 | 38 | 46.6 | 49.1 | 42.3 | 45.9 | 49.7 | 44.7 | 38 | 39.9 | 27.5 | 38.5 | 49.2 | 50.2 | 42.6 | 50
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 65 | 51 | 37.3 | 34.7 | 53 | 59.2 | 63.7 | 59.3 | 56.8 | 58.8 | 59.9 | 55 | -31.4 | 40.2 | 0 | 0 | 58.1 | 0 | 57.1 | 63.8 | 58.9 | 43.7 | 60.2 | 66
Total ROR | 100.64 | 75.64 | 100.64 | 110.74 | 110.74 | 111.64 | 174.34 | 196.24 | 215.64 | 229.54 | 286.24 | 312.94 | 293.34 | 270.04 | 285.34 | 321.34 | 238.84 | 233.84 | 213.24 | 273.04 | 171.44 | 171.44 | 290.74 | 353.84 | 353.84 | 326.94 | 312.54 | 267.74 | 219.64 | 183.04 | 153.14 | 489.91 | 353.84 | 75.64 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.27083: 0; 0.29167: 0; 0.3125: 0 | 60 | 0 | 0 | [15 empty] | 370 | 375 | 385 | 398 | 435 | 411.2 | 200 | 7.6 | 113.2 | 364.3 | 410 | 412 | 457 | 480.8 | 503 | 449.3 | 469 | 422 | 284.5 | 287 | 360 | 334 | 410 | 320
KL2(32) | 0.27083: 4.5; 0.29167: 0; 0.3125: 0 | 32 | 4.5 | 0 | [15 empty] | 3 | 3.1 | 3.8 | 3.1 | 3.8 | 9.3 | 39.5 | 20.9 | 18 | 20 | 40 | 43.2 | 45.7 | 41.8 | 51.9 | 28.2 | 23.8 | 21 | 17.7 | 39.2 | 45 | 2.8 | 17.1 | 3
KL3(14) | 0.27083: 1.6; 0.29167: 0; 0.3125: 0 | 14 | 1.6 | 0 | [15 empty] | 108 | 14 | 0 | 0 | 0 | 11 | 16.7 | 0 | 0 | 0 | 0 | 0 | 87 | 107.6 | 107.4 | 91.6 | 65.8 | 59.2 | 59 | 92 | 91 | 92 | 0 | 108
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 6.1 | 0 | [15 empty] | 55 | 55.8 | 49 | 55 | 44.8 | 49.4 | 38.5 | 38.7 | 36 | 38 | 46.6 | 49.1 | 42.3 | 45.9 | 49.7 | 44.7 | 38 | 39.9 | 27.5 | 38.5 | 49.2 | 50.2 | 42.6 | 50
TANAKPUR | 66 | 65 | 51 | 37.3 | 34.7 | 53 | 57.2 | 59.2 | 51.7 | 63.7 | 56.2 | 59.3 | 56.8 | 58.8 | 59.9 | 55 | -31.4 | 40.2 | 0 | 0 | 58.1 | 57.8 | 0 | 0 | 57.1 | 62.5 | 63.8 | 59.3 | 58.9 | 43.7 | 60.2 |  | 66 | -31.4
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 320 | 370 | 375 | 385 | 398 | 435 | 455 | 411.2 | 404.8 | 200 | 62.2 | 7.6 | 113.2 | 364.3 | 410 | 412 | 457 | 480.8 | 503 | 449.3 | 469 | 434.1 | 422 | 387.3 | 284.5 | 270.9 | 287 | 285 | 360 | 334 | 410 |  | 503 | 7.6
RAMNAGAR | 3 | 3 | 3.1 | 3.8 | 3.1 | 3.8 | 2.9 | 9.3 | 32.6 | 39.5 | 22.8 | 20.9 | 18 | 20 | 40 | 43.2 | 45.7 | 41.8 | 51.9 | 28.2 | 23.8 | 21.7 | 21 | 18 | 17.7 | 29 | 39.2 | 50.2 | 45 | 2.8 | 17.1 |  | 51.9 | 2.8 | [22 empty] | 65 | 0 | 370 | 3 | 108 | 55
RAXAUL 132 | 108 | 108 | 14 | 0 | 0 | 0 | 0 | 11 | 16.8 | 16.7 | 0 | [5 empty] | 87 | 107.6 | 107.4 | 91.6 | 65.8 | 59.2 | 59.2 | 60 | 59 | 88.2 | 92 | 93 | 91 | 92 | 0 |  | 108 | 0 | [22 empty] | 51 | 0 | 375 | 3.1 | 14 | 55.8
NANPARA(33kV) | 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0 | [22 empty] | 37.3 | 0 | 385 | 3.8 | 0 | 49
BISHANPUR(33kV) | 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0 |  | UTK Discharge Test | [20 empty] | 34.7 | 0 | 398 | 3.1 | 0 | 55
JALESHWOR(33kV) | 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0 | [22 empty] | 53 | 0 | 435 | 3.8 | 0 | 44.8
RAJBIRAJ(33kV) | 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0 | Line1 | [21 empty] | 59.2 | 0 | 411.2 | 9.3 | 11 | 49.4
RAXAUL(33kV) | 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0 | Line 2 | [21 empty] | 63.7 | 0 | 200 | 39.5 | 16.7 | 38.5
SAMPATIYA 132 kV | 50 | 54.5 | 55.8 | 49 | 55 | 44.8 | 50.7 | 49.4 | 45.8 | 38.5 | 37.3 | 38.7 | 36 | 38 | 46.6 | 49.1 | 42.3 | 45.9 | 49.7 | 44.7 | 38 | 39.9 | 39.9 | 32.1 | 27.5 | 28.4 | 38.5 | 44 | 49.2 | 50.2 | 42.6 |  | 55.8 | 27.5 | [22 empty] | 59.3 | 0 | 7.6 | 20.9 | 0 | 38.7
Total IMPORT | 547 | 600.5 | 498.9 | 475.1 | 490.8 | 536.6 | 565.8 | 540.1 | 551.7 | 358.4 | 178.5 | 126.5 | 224 | 481.1 | 556.5 | 559.3 | 632 | 716.3 | 712 | 613.8 | 654.7 | 612.7 | 542.1 | 497.4 | 445.8 | 479 | 520.5 | 531.5 | 604.1 | 522.7 | 529.9 | 0 | 716.3 | 126.5 | [22 empty] | 56.8 | 0 | 113.2 | 18 | 0 | 36
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 58.8 | 0 | 364.3 | 20 | 0 | 38
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 59.9 | 0 | 410 | 40 | 0 | 46.6
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 55 | 0 | 412 | 43.2 | 0 | 49.1
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | -31.4 | 0 | 457 | 45.7 | 87 | 42.3
TOTAL SYSTEM LOAD (ACTUAL) | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1246.99 | 1275.29 | 1362.69 | 1397.19 | 1375.39 | 1406.09 | 1328.19 | 1275.59 | 1427.29 | 1470.09 | 1380.29 | 1459.09 | 1434.19 | 1395.79 | 1335.09 | 1293.09 | 1341.79 | 1446.59 | 1404.99 | 1431.29 | 1482.79 | 1442.29 | 1421.79 | 1248.79 | 1206.09 | 2231.81 | 1482.79 | 1097.89 | [22 empty] | 40.2 | 0 | 480.8 | 41.8 | 107.6 | 45.9
Interruption/Tripping | 0.3125: 180; 0.33333: 180; 0.375: 180; 0.41667: 140; 0.45833: 120; 0.72917: 150; 0.75: 270; 0.77083: 270; 0.79167: 270; 0.8125: 150; 0.83333: 0 |  | 270 | 0 | [22 empty] | 0 | 0 | 503 | 51.9 | 107.4 | 49.7
TOTAL SYSTEM LOAD (EXPECTED) | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1246.99 | 1275.29 | 1362.69 | 1397.19 | 1555.39 | 1586.09 | 1508.19 | 1415.59 | 1547.29 | 1470.09 | 1380.29 | 1459.09 | 1434.19 | 1395.79 | 1335.09 | 1443.09 | 1611.79 | 1716.59 | 1674.99 | 1581.29 | 1482.79 | 1442.29 | 1421.79 | 1248.79 | 1206.09 | 1693.71 | 1716.59 | 1097.89 | [22 empty] | 0 | 0 | 449.3 | 28.2 | 91.6 | 44.7
TOTAL NATIONAL LOAD (ACTUAL) | 1159.19 | 1187.69 | 1111.09 | 1097.89 | 1107.59 | 1155.09 | 1246.99 | 1275.29 | 1362.69 | 1397.19 | 1555.39 | 1586.09 | 1508.19 | 1415.59 | 1547.29 | 1470.09 | 1348.89 | 1459.09 | 1434.19 | 1395.79 | 1335.09 | 1443.09 | 1611.79 | 1716.59 | 1674.99 | 1581.29 | 1482.79 | 1442.29 | 1421.79 | 1248.79 | 1206.09 |  | 1716.59 | 1097.89 | [22 empty] | 58.1 | 0 | 469 | 23.8 | 65.8 | 38
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 0 | 0 | 422 | 21 | 59.2 | 39.9
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 57.1 | 0 | 284.5 | 17.7 | 59 | 27.5
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 63.8 | 0 | 287 | 39.2 | 92 | 38.5
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58.9 | 0 | 360 | 45 | 91 | 49.2
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31.4 | 0 | [22 empty] | 43.7 | 0 | 334 | 2.8 | 92 | 50.2
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 60.2 | 0 | 410 | 17.1 | 0 | 42.6
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31.4 | 0 | [22 empty] | 66 | 0 | 320 | 3 | 108 | 50
NET IMPORT | 547 | 600.5 | 498.9 | 475.1 | 490.8 | 536.6 | 565.8 | 540.1 | 551.7 | 358.4 | 178.5 | 126.5 | 224 | 481.1 | 556.5 | 559.3 | 600.6 | 716.3 | 712 | 613.8 | 654.7 | 612.7 | 542.1 | 497.4 | 445.8 | 479 | 520.5 | 531.5 | 604.1 | 522.7 | 529.9 |  | 716.3 | 126.5
HZ | 50.087 | 50.087 | 49.999 | 50.062 | 50.022 | 50.037 | 50.074 | 50.097 | 49.978 | 50.004 | 50.049 | 50.108 | 50.163 | 50.016 | 50.075 | 50.021 | 50.163 | 50.231 | 50.04 | 49.93 | 49.94 | 50.11 | 50.02 | 50 | 50.01 | 50.04 | 50.08 | 49.957 | 50.068 | 50.033 | 50.005 |  | 50.231 | 49.93
HTD 132KV | 132.7 | 132.7 | 129.7 | 128 | 129 | 126.8 | 125.8 | 128.8 | 126.6 | 130.8 | 125.7 | 124.8 | 125.4 | 125.4 | 122.9 | 123.2 | 124.9 | 125.6 | 125.4 | 125.8 | 126.8 | 127.8 | 129 | 127.5 | 127.7 | 129.6 | 129.5 | 130.1 | 129.8 | 130.4 | 127.5 |  | 132.7 | 122.9
SUI 132KV | 135.7 | 135.7 | 133.6 | 132.6 | 132.9 | 130.9 | 130.4 | 132.2 | 129.7 | 132 | 127.8 | 127 | 127.8 | 127.7 | 126.1 | 126.2 | 128.6 | 128.5 | 127.9 | 128.3 | 128.9 | 129.4 | 129.8 | 128.3 | 128.5 | 129.5 | 131 | 131.7 | 132.1 | 133.1 | 131.7 |  | 135.7 | 126.1
DUBI 132KV | 131.4 | 131.4 | 131.2 | 131.2 | 131.4 | 128.2 | 125.3 | 128.8 | 126 | 129.7 | 126.2 | 126.8 | 127.2 | 126.8 | 122 | 127.4 | 127.7 | 124.5 | 126.9 | 125.7 | 129.1 | 131.6 | 129.3 | 127.7 | 128.7 | 126.3 | 128.5 | 128.7 | 127.6 | 129.1 | 128 |  | 131.6 | 122
ANAMANI 132KV | 133.1 | 133.1 | 132.9 | 133.6 | 133.2 | 130.2 | 127.2 | 130.8 | 127 | 127.6 | 124.3 | 124.5 | 124.5 | 125 | 121.6 | 126.3 | 127.5 | 123.9 | 125.9 | 126 | 128 | 130.9 | 127.7 | 126 | 127.6 | 127 | 130 | 131.2 | 130.6 | 132.2 | 131.5 |  | 133.6 | 121.6
KG-A 132KV | 135 | 135 | 135 | 132.9 | 132.6 | 132.1 | 133.6 | 136.8 | 136 | 136 | 130.6 | 131.7 | 131.7 | 130.7 | 131.3 | 132.2 | 131.1 | 131.1 | 133.1 | 133 | 134.3 | 135.5 | 135.8 | 132.3 | 132.2 | 132.2 | 134.8 | 134.9 | 133.7 | 132.9 | 131.7 |  | 136.8 | 130.6
KOHALPUR 132KV | 130.6 | 130.6 | 130.6 | 131.5 | 134.6 | 129.3 | 134.5 | 128 | 134.6 | 131.8 | 135.4 | 133.8 | 130.3 | 126.4 | 124.1 | 132 |  | 129.2 | 130.3 | 127 | 132 | 132.5 | 0 | 131.4 | 132.4 | 132.4 | 134.6 | 134.5 | 131.8 | 134.2 | 130.7 |  | 135.4 | 0
SUI 66KV | 68.3 | 68.3 | 68.3 | 66.9 | 67 | 66.1 | 65.7 | 66.6 | 65.3 | 65.5 | 64 | 63.7 | 64 | 64 | 63.7 | 63.2 | 64.2 | 64.6 | 64.2 | 64.3 | 64.4 | 64.9 | 65.3 | 64.4 | 64.5 | 64.5 | 65.7 | 66.1 | 66.3 | 66.9 | 66.2 |  | 68.3 | 63.2
[33 empty] | 0 | 0
Kathmandu Load | 138.44 | 149.44 | 116.14 | 124.194 | 133.469 | 157.459 | 186.195 | 220.789 | 266.879 | 311.15 | 351.515 | 357.24 | 345.7 | 331.66 | 42 | 314.34 | 306.38 | 286.321 | 302.8 | 299.04 | 311.34 | 351.32 | 369.9 | 396.64 | 390.34 | 374.74 | 351.04 | 333.293 | 275.376 | 209.113 | 171.997 |  | 396.64 | 42
MRS-SYU | -8.1 | -5 | -4.3 | -1.9 | -2.2 | -1.3 | 14.4 | 17.1 | 29.6 | 34.6 | 37.4 | 43.9 | 41.1 | 40 | 45.3 | 48.2 | 27.2 | 30 | 19.2 | 27.2 | 24.5 | 24.2 | 42.1 | 41.5 | 55.4 | 48.3 | 41.2 | 34.8 | 24.2 | 12.1 | 6.9 | 75 | 55.4 | -8.1
NMRS-MATA | -15 | -10 | -7 | -3 | -4.3 | -2.8 | 17.1 | 19.5 | 35.7 | 47.6 | 49.5 | 60 | 58.3 | 56 | 57.7 | 62.1 | 33.8 | 37.5 | 27.8 | 36.4 | 34.9 | 34.1 | 56.7 | 55.9 | 74.3 | 65 | 56.8 | 48 | 27.4 | 13.4 | 6.1 | 240 | 74.3 | -15
KL2-MATA | -7 | -10 | -32 | -44 | -37.1 | -31 | -36 | -16.2 | -14.2 | 14 | 16.5 | 14 | 15.6 | 19.8 | -4.6 | -10 | 21.8 | 8.9 | 25 | 19 | 32 | 51 | 53 | 59 | 49 | 46 | 29.3 | 23 | 13 | -6 | -31 | 240 | 59 | -44
KL1-SYU | 1.1 | 2 | -8 | -8.9 | -9 | -6.2 | -10.4 | 2.8 | 7.8 | 19.4 | 19.6 | 20.4 | 19.3 | 20.5 | 9.9 | 4 | 5.2 | 7.5 | 9.4 | 10.5 | 11 | 26.2 | 28.4 | 30.7 | 30.9 | 32.3 | 29.6 | 27.6 | 13.9 | 5.6 | -2.2 | 60 | 32.3 | -10.4
KHIMTI-LAMOSANGHU | 80 | 85 | 80 | 93.854 | 98.029 | 109.719 | 111.055 | 108.049 | 119.739 | 105.21 | 137.775 | 128 | 121.36 | 103.32 | 106.6 | 116.8 | 124.64 | 111.981 | 123.36 | 112.8 | 118.4 | 125.28 | 100.16 | 120 | 91.2 | 93.6 | 100 | 93.353 | 101.536 | 86.673 | 95.357 | 120 | 137.775 | 80
LAMOSHANGU-BHAKTAPUR | 65 | 70 | 72 | 69.5 | 71.4 | 77.5 | 77.3 | 75.4 | 82.9 | 74.7 | 90.2 | 89 | 82.7 | 74.4 | 77 | 84.1 | 85.6 | 80 | 85.5 | 80.2 | 83.7 | 87.3 | 73.8 | 83.2 | 68.8 | 71.1 | 71.7 | 69.4 | 74.2 | 67.3 | 72.5 |  | 90.2 | 65
BALAJU-SYUCHATAR | 50 | 60 | 58 | 58.3 | 57.3 | 53 | 33.3 | 27.2 | 8 | -22.8 | -14.1 | -23 | -22.5 | -25.5 | -1.3 | -7 | 2.2 | -2.4 | 9.8 | 0 | -6.3 | -15.6 | -48.8 | -47.2 | -68.9 | -57.9 | -36.9 | -30.2 | -1.4 | 21.1 | 47.1 |  | 60 | -68.9
DHALKE-NAWALPUR I | 66 | 86 | 66 | 89.1 | 83.3 | 102 | 98 | 86.8 | 92.3 | 61.7 | 76 | 71 | 70.2 | 75.7 | 88.6 | 91 | 86.4 | 75.8 | 84 | 74.7 | 81.5 | 88.7 | 85.4 | 58.9 | 47.3 | 47.1 | 59.5 | 52.4 | 61 | 55.8 | 85 |  | 102 | 47.1
N. BHARATPUR-BARDGHAT I | 20 | 15 | 18 | 14.6 | 14 | 10.5 | -1.3 | -3.8 | -13.6 | -11.4 | -12.1 | -17 | -14.8 | -12.7 | -17.5 | -24 | -1.8 | -3.6 | 5.4 | 0 | -1.2 | 0 | 1.7 | -6.1 | -22.6 | -20.3 | -9.8 | -3.4 | 4.9 | 13.6 | 19.5 |  | 20 | -24
DAMAK-DUHABI | -10 | -8 | -7 | -6.9 | -8.6 | -12.5 | -17.1 | -26.1 | -38.3 | -44.4 | -50.5 | -48.7 | -43.1 | -36.9 | -27.6 | -25 | -24.8 | -26.8 | -29.4 | -27.8 | -35.1 | -35.2 | -46.7 | -56 | -46 | -41.1 | -34.6 | -30.1 | -23.8 | -17.6 | -12.1 |  | -6.9 | -56
HETAUDA-KAMANE | -18 | 2 | 1.6 | 11.8 | 6.5 | 4.7 | 16.3 | 6.1 | 13.4 | 0 | -1 | 3.1 | 0 | -5.3 | 12.4 | 18 | -20.5 | -19.3 | -30.9 | -16.3 | -32.1 | -37.5 | -38.9 | -33.7 | -15.3 | -13.7 | -9.2 | -5.7 | -18.6 | -10.7 | 4.7 |  | 18 | -38.9
MIRCHAIYA LAHAN 2 | 82 | 80 | 82 | 82.5 | 80.4 | 91.8 | 98.9 | 97 | 116.7 | 99.6 | 111.3 | 106 | 99.5 | 98.8 | 120.3 | 112 | 114.7 | 115.4 | 108.3 | 111 | 102.9 | 102.1 | 100.6 | 119 | 108.4 | 113 | 119.5 | 120.9 | 116.1 | 107 | 90.9 |  | 120.9 | 80
Water Level
UTK | 1984.7 | 1984.92 | 1985.15 | 1985.39 | 1985.57 | 1985.79 |  | 1985.95 |  | 1985.88 |  | 1985.12 | 1984.05 | 1983.6 | 1983.7 | 1983.7 | 1983.8 | 1984.02 | 1984.28 | 1984.5 | 1984.71 |  | 1984.94 |  | 1984.9 |  | 1984.5 |  | 1984.7 | 1984.79 | 1984.98
KGA | 522.04 | 522.36 | 522.63 | 522.96 | 523.23 | 523.54 |  | 523.62 |  | 523.57 |  | 523.42 | 523.14 | 522.87 | 522.66 | 522.35 | 522.14 | 522.11 | 522.02 | 521.9 | 521.69 |  | 521.8 |  | 521.35 |  | 520.82 |  | 520.7 | 520.82 | 520.94
MMRS | 622.77 | 623.01 | 623.14 | 623.1 | 623.1 | 623.09 |  | 623 |  | 623.02 |  | 623.02 | 623.03 | 623.01 | 622.99 | 623 | 622.99 | 623.04 |  | 623.21 | 623.3 |  | 623.35 |  | 623.42 |  | 623.43 |  | 623.41 | 623.41 | 623.41
MRS | 335.64 | 335.95 | 336.27 | 336.54 | 336.8 | 337.02 |  | 337.17 |  | 337.12 |  | 336.89 | 336.7 | 336.56 | 336.38 | 336.04 | 335.8 | 335.68 | 335.49 | 335.54 | 335.49 |  | 335.6 |  | 335.37 |  | 335.2 |  | 334.95 | 334.87 | 334.85
CHM | 883.8 | 884.5 | 885.1 | 885.7 | 886.4 | 886.4 |  | 886.8 |  | 887.8 |  | 887.8 | 887.5 | 887.3 | 887.2 | 887 | 886.8 | 886.8 | 886.9 | 886.7 | 886.3 |  | 886.4 |  | 885.9 |  | 884.6 | 883.6 | 883.6 | 883.8 | 884.9
KL 1 | 0.83333: 1519.69
Others IPP Detail
Upper Mai Khola(9.98) | 0.5: 0; 0.54167: 0.1; 0.58333: 0.22; 0.625: 0.26; 0.66667: 0.22 | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9) | 0.27083: 378
Sipring Khola(9.658) | 0.27083: 250
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.22 | 0.26 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1586.09; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/20)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 21
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/21 |  |  | 2080/10/21 |  |  | Monday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 522.9 | 504.7 | 513.7 | 528 | 549.3 | 535.8 | 561.6 | 546.2 | 280.6 | 184.2 | 140.6 | 286.2 | 520.2 | 516.3 | 624.6 | 695.2 | 719 | 731 | 733.5 | 748.9 | 710.1 | 750 | 725.4 | 577.4 | 421.4 | 398.8 | 562.3 | 548.9 | 649.7 | 661.1 | 487
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1675MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1111 | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1255.59 | 1347.39 | 1444.39 | 1474.69 | 1674.73 | 1628.73 | 1567.29 | 1477.19 | 1428.39 | 1379.59 | 1451.59 | 1420.49 | 1424.49 | 1441.49 | 1466.99 | 1431.69 | 1507.19 | 1704.85 | 1747.15 | 1675.99 | 1601.99 | 1525.29 | 1489.09 | 1394.79 | 1302.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1628.73 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1628.73 MW
Solu Khola Dudhkoshi(86) | 26.1 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 28.5 | 28.4 | 27.2 | 27.2 | 27.2 | 27.2 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 86 | 30.4 | 26.1
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 21
Super Dordi (54) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 54 | 10.5 | 9.7 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/21)
Likhu-IV(52.4) | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 52.4 | 14.8 | 12.1
Upper Marsyangdi "A"(50) | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 50 | 25.5 | 25.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 45 | 17.1 | 14 |  | IPP | 447.8 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.95 | 488.85 | 487.65 | 487.65
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 49.1 | 84.1 | 304.2 | 490.1 | 304.1 | 64.1 | 64
Mistri Khola(42) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 42 | 6.6 | 6.5 |  | NEA ROR PROR | 142.24 | 119.04 | 118.04 | 118.04 | 132.04 | 144.04 | 213.44 | 301.64 | 259.08 | 238.14 | 205.24 | 210.44
Upper Chameliya(40) | 0 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 0 |  | IMPORT | 487 | 522.9 | 504.7 | 513.7 | 528 | 549.3 | 561.6 | 280.6 | 140.6 | 286.2 | 520.2 | 516.3
Upper Kalanga Gad(38.46) | 0 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 0 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 250 | 250 | 200 | 150
Nyadi(30) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 30 | 9.1 | 7 |  | System_Load | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1347.39 | 1474.69 | 1628.73 | 1567.29 | 1477.19 | 1428.39
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 28 | 7.3 | 6.8 |  | National_Load | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1347.39 | 1474.69 | 1628.73 | 1567.29 | 1477.19 | 1428.39
Dordi(27) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 30 | 8.7 | 6.1
Upper Madi(25) | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 11.1 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 25 | 8.6 | 6.8
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 19.8 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 0 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 0
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 0
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 0 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 0
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 0 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 0
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 17.8 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 20.1 | 20.1 | 18.2 | 18.9 | 19.8 | 21 | 22.1 | 18.3 | 24.4 | 22.2 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 17 | 17 | 17 | 17 | 17 | 17 | 240 | 24.4 | 17
Total IPP | 447.8 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.25 | 488.95 | 488.85 | 487.65 | 487.65 | 487.65 | 487.65 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 1042.4 | 488.95 | 447.8
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 50 | 80 | 270 | 380 | 456 | 270 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 230 | 370 | 340 | 140 | 120 | 0 | 0 | 456 | 456 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.2 | 7.1 | 7.1 | 7.1 | 7 | 7 | 6.3 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 12.2 | 14.2 | 22.1 | 19.8 | 5.6
Total NEA SUBSIDIARIES | 34.1 | 34.1 | 34.1 | 34.1 | 34.1 | 49.1 | 59.1 | 84.1 | 114.1 | 304.2 | 414.2 | 490.1 | 304.1 | 64.1 | 64 | 34 | 33.3 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 132.6 | 276.8 | 416.8 | 386.8 | 186.8 | 166.8 | 39.2 | 41.2 | 538.1 | 490.1 | 32.6
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 28.3 | 40.4 | 97.7 | 114.8 | 140.5 | 70.7 | 48.2 | 30.7 | 31 | 60 | 60 | 30.8 | 61 | 81 | 89 | 61.6 | 88 | 145.1 | 145.1 | 134 | 118.1 | 117.8 | 117.4 | 47.8 | 0 | 144 | 145.1 | 0
Middle MRS(70) | 35.3 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 34.8 | 35 | 34.9 | 34.9 | 35.1 | 35.3 | 35.3 | 35.3 | 24.8 | 35.2 | 35.1 | 35.1 | 35.1 | 35.1 | 25 | 35 | 35 | 35 | 35 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 70 | 35.3 | 24.8
MRS(69) | 22 | 0 | 0 | 0 | 0 | 16 | 16.1 | 45.9 | 65.8 | 54.9 | 58.3 | 48.9 | 50.3 | 34.2 | 34.2 | 34.4 | 34.2 | 34.6 | 0 | 0 | 0 | 0 | 0 | 60.2 | 69.1 | 62.2 | 61.8 | 69.2 | 69.2 | 64.5 | 0 | 69 | 69.2 | 0
U Trisuli 3A(60) | 40.9 | 39.8 | 38.8 | 38.8 | 38.8 | 38.8 | 38.8 | 38 | 38 | 38 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 35 | 33 | 33 | 33 | 33 | 35.3 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 40.3 | 43.3 | 60 | 43.3 | 33
CHM(30) | 0 | 0 | 0 | 0 | 14 | 10 | 10 | 10.3 | 10.3 | 15 | 23.3 | 23.3 | 10.3 | 10.7 | 10.3 | 14.9 | 10 | 9.8 | 10.2 | 10.2 | 15 | 10 | 10 | 15 | 15 | 15 | 10 | 12.7 | 10.3 | 10.3 | 14.1 | 30 | 23.3 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0.74 | 13.7 | 14 | 19.3 | 20.2 | 19 | 17.5 | 13.5 | 8 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20.2 | 0 | [14 empty] | Tanakpur | 50 | 56.1 | 62.4 | 66.4 | 61.6 | 66 | 47.8 | 54.2 | 67.3 | 51.6 | 60.6 | 58.6 | 54.8 | 58.1 | 61.7 | 58 | 76.2 | 59.3 | 70.3 | 64.6 | 59.7 | 61.7 | 61.4 | 0
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 15 | 4.5 | 4.5 | [14 empty] | Muz | 390 | 397.2 | 401.6 | 411 | 419.4 | 419.7 | 150 | 1 | 119 | 365.7 | 362.2 | 424 | 442 | 457.6 | 475 | 471.3 | 457 | 489 | 301 | 139.8 | 294.5 | 372.9 | 404.6 | 412
DEVI(14.1) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 14.1 | 11.2 | 11.2 | [14 empty] | Ram | 28 | 2.8 | 2.7 | 0 | 16.9 | 21.2 | 42.3 | 33.4 | 30 | 28 | 24.5 | 18 | 20.8 | 15.4 | 14.2 | 22.4 | 17.4 | 23.1 | 24.1 | 22.7 | 22.1 | 20.8 | 23.7 | 20
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 14 | 3.3 | 3.3 | [14 empty] | Rax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 115 | 115 | 103 | 102 | 120 | 105 | 100 | 96.8 | 105.6 | 121.6 | 118.8 | 0
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 55 | 48.6 | 47 | 50.6 | 51.4 | 54.7 | 40.5 | 52 | 69.9 | 74.9 | 69 | 60 | 62.6 | 72.9 | 77.1 | 79.8 | 78.3 | 73.6 | 82 | 74.9 | 67 | 72.7 | 52.6 | 55
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 50 | 56.1 | 62.4 | 66.4 | 61.6 | 66 | 47.8 | 54.2 | 67.3 | 51.6 | 60.6 | 58.6 | 54.8 | 58.1 | 61.7 | 58 | 76.2 | 59.3 | 70.3 | 64.6 | 59.7 | 61.7 | 61.4 | 0
Total ROR | 142.24 | 119.04 | 118.04 | 118.04 | 132.04 | 144.04 | 172.44 | 213.44 | 290.84 | 301.64 | 338.08 | 259.08 | 238.14 | 205.24 | 210.44 | 233.34 | 235.44 | 204.84 | 196.84 | 211.34 | 221.44 | 174.94 | 210.54 | 332.8 | 343.7 | 323.74 | 302.34 | 312.14 | 309.34 | 241.84 | 136.34 | 489.91 | 343.7 | 118.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.79167: 29.3 | 60 | 29.3 | 0 | [15 empty] | 390 | 397.2 | 401.6 | 411 | 419.4 | 419.7 | 150 | 1 | 119 | 365.7 | 362.2 | 424 | 442 | 457.6 | 475 | 471.3 | 457 | 489 | 301 | 139.8 | 294.5 | 372.9 | 404.6 | 412
KL2(32) | 0.27083: 3.7; 0.29167: 0; 0.3125: 0; 0.79167: 4.3 | 32 | 4.3 | 0 | [15 empty] | 28 | 2.8 | 2.7 | 0 | 16.9 | 21.2 | 42.3 | 33.4 | 30 | 28 | 24.5 | 18 | 20.8 | 15.4 | 14.2 | 22.4 | 17.4 | 23.1 | 24.1 | 22.7 | 22.1 | 20.8 | 23.7 | 20
KL3(14) | 0.27083: 1.3; 0.29167: 0; 0.3125: 0; 0.79167: 1.6 | 14 | 1.6 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 115 | 115 | 103 | 102 | 120 | 105 | 100 | 96.8 | 105.6 | 121.6 | 118.8 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 35.2 | 0 | [15 empty] | 55 | 48.6 | 47 | 50.6 | 51.4 | 54.7 | 40.5 | 52 | 69.9 | 74.9 | 69 | 60 | 62.6 | 72.9 | 77.1 | 79.8 | 78.3 | 73.6 | 82 | 74.9 | 67 | 72.7 | 52.6 | 55
TANAKPUR | 0 | 50 | 56.1 | 62.4 | 66.4 | 61.6 | 52.3 | 66 | 63.3 | 47.8 | 52.6 | 54.2 | 67.3 | 51.6 | 60.6 | 58.6 | 54.8 | 58.1 | 61.7 | 58 | 76.2 | 59 | 59.3 | 62.8 | 70.3 | 46.5 | 64.6 | 57.1 | 59.7 | 61.7 | 61.4 |  | 76.2 | 0
KATAIYA | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0 |  | 0 | 0
MUJAFFARPUR | 412 | 390.1 | 397.2 | 401.6 | 411 | 419.4 | 409 | 419.7 | 389.5 | 150 | 52.9 | 1 | 119 | 365.7 | 362.2 | 424 | 442 | 457.6 | 475 | 471.3 | 457 | 461 | 489 | 443 | 301 | 160 | 139.8 | 294.8 | 294.5 | 372.9 | 404.6 |  | 489 | 1
RAMNAGAR | 20 | 27.6 | 2.8 | 2.7 | 0 | 16.9 | 22.5 | 21.2 | 44.4 | 42.3 | 36.2 | 33.4 | 30 | 28 | 24.5 | 18 | 20.8 | 15.4 | 14.2 | 22.4 | 17.4 | 17.8 | 23.1 | 38.6 | 24.1 | 24 | 22.7 | 21.6 | 22.1 | 20.8 | 23.7 |  | 44.4 | 0 | [22 empty] | 50 | 0 | 390 | 28 | 0 | 55
RAXAUL 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 64 | 115 | 115 | 103 | 102 | 120 | 97 | 105 | 103 | 100 | 114 | 96.8 | 114.8 | 105.6 | 121.6 | 118.8 |  | 121.6 | 0 | [22 empty] | 56.1 | 0 | 397.2 | 2.8 | 0 | 48.6
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 62.4 | 0 | 401.6 | 2.7 | 0 | 47
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 66.4 | 0 | 411 | 0 | 0 | 50.6
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 61.6 | 0 | 419.4 | 16.9 | 0 | 51.4
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 66 | 0 | 419.7 | 21.2 | 0 | 54.7
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 47.8 | 0 | 150 | 42.3 | 0 | 40.5
SAMPATIYA 132 kV | 55 | 55.2 | 48.6 | 47 | 50.6 | 51.4 | 52 | 54.7 | 49 | 40.5 | 42.5 | 52 | 69.9 | 74.9 | 69 | 60 | 62.6 | 72.9 | 77.1 | 79.8 | 78.3 | 75.3 | 73.6 | 78 | 82 | 76.9 | 74.9 | 74 | 67 | 72.7 | 52.6 |  | 82 | 40.5 | [22 empty] | 54.2 | 0 | 1 | 33.4 | 0 | 52
Total IMPORT | 487 | 522.9 | 504.7 | 513.7 | 528 | 549.3 | 535.8 | 561.6 | 546.2 | 280.6 | 184.2 | 140.6 | 286.2 | 520.2 | 516.3 | 624.6 | 695.2 | 719 | 731 | 733.5 | 748.9 | 710.1 | 750 | 725.4 | 577.4 | 421.4 | 398.8 | 562.3 | 548.9 | 649.7 | 661.1 | 0 | 750 | 140.6 | [22 empty] | 67.3 | 0 | 119 | 30 | 0 | 69.9
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 51.6 | 0 | 365.7 | 28 | 0 | 74.9
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 60.6 | 0 | 362.2 | 24.5 | 0 | 69
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 58.6 | 0 | 424 | 18 | 64 | 60
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0 | [22 empty] | 54.8 | 0 | 442 | 20.8 | 115 | 62.6
TOTAL SYSTEM LOAD (ACTUAL) | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1255.59 | 1347.39 | 1444.39 | 1374.69 | 1424.73 | 1378.73 | 1317.29 | 1277.19 | 1278.39 | 1379.59 | 1451.59 | 1420.49 | 1424.49 | 1441.49 | 1466.99 | 1381.69 | 1457.19 | 1654.85 | 1697.15 | 1625.99 | 1551.99 | 1525.29 | 1489.09 | 1394.79 | 1302.69 | 2231.81 | 1697.15 | 1111.14 | [22 empty] | 58.1 | 0 | 457.6 | 15.4 | 115 | 72.9
Interruption/Tripping | 0.29167: 100; 0.3125: 250; 0.33333: 250; 0.375: 250; 0.41667: 200; 0.45833: 150; 0.72917: 50; 0.75: 50; 0.77083: 50; 0.79167: 50; 0.8125: 50; 0.83333: 50 |  | 250 | 50 | [22 empty] | 61.7 | 0 | 475 | 14.2 | 103 | 77.1
TOTAL SYSTEM LOAD (EXPECTED) | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1255.59 | 1347.39 | 1444.39 | 1474.69 | 1674.73 | 1628.73 | 1567.29 | 1477.19 | 1428.39 | 1379.59 | 1451.59 | 1420.49 | 1424.49 | 1441.49 | 1466.99 | 1431.69 | 1507.19 | 1704.85 | 1747.15 | 1675.99 | 1601.99 | 1525.29 | 1489.09 | 1394.79 | 1302.69 | 1693.71 | 1747.15 | 1111.14 | [22 empty] | 58 | 0 | 471.3 | 22.4 | 102 | 79.8
TOTAL NATIONAL LOAD (ACTUAL) | 1111.14 | 1164.29 | 1145.09 | 1154.09 | 1182.39 | 1230.69 | 1255.59 | 1347.39 | 1444.39 | 1474.69 | 1674.73 | 1628.73 | 1567.29 | 1477.19 | 1428.39 | 1379.59 | 1451.59 | 1420.49 | 1424.49 | 1441.49 | 1466.99 | 1431.69 | 1507.19 | 1704.85 | 1747.15 | 1675.99 | 1601.99 | 1525.29 | 1489.09 | 1394.79 | 1302.69 |  | 1747.15 | 1111.14 | [22 empty] | 76.2 | 0 | 457 | 17.4 | 120 | 78.3
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 59.3 | 0 | 489 | 23.1 | 105 | 73.6
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 70.3 | 0 | 301 | 24.1 | 100 | 82
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 64.6 | 0 | 139.8 | 22.7 | 96.8 | 74.9
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 59.7 | 0 | 294.5 | 22.1 | 105.6 | 67
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61.7 | 0 | 372.9 | 20.8 | 121.6 | 72.7
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61.4 | 0 | 404.6 | 23.7 | 118.8 | 52.6
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 0 | 0 | 412 | 20 | 0 | 55
NET IMPORT | 487 | 522.9 | 504.7 | 513.7 | 528 | 549.3 | 535.8 | 561.6 | 546.2 | 280.6 | 184.2 | 140.6 | 286.2 | 520.2 | 516.3 | 624.6 | 695.2 | 719 | 731 | 733.5 | 748.9 | 710.1 | 750 | 725.4 | 577.4 | 421.4 | 398.8 | 562.3 | 548.9 | 649.7 | 661.1 |  | 750 | 140.6
HZ | 50.005 | 50.024 | 49.985 | 49.96 | 50.03.6 | 50.04 | 50.0106 | 50.062 | 49.952 | 49.963 | 50 | 50.054 | 50.064 | 50.04 | 50.015 | 50.023 | 50.23 | 49.991 | 49.985 | 49.946 | 49.895 | 50.033 | 50.089 | 50.057 | 49.996 | 50.046 | 50.06 | 50.03 | 50.09 | 50 | 49.98 |  | 50.23 | 49.895
HTD 132KV | 128 | 128 | 126.3 | 127.8 | 127.8 | 127.8 | 126 | 126 | 125.9 | 129.6 | 127 | 124.7 | 127 | 126.6 | 126.1 | 124.9 | 124.1 | 124.6 | 123.7 | 124.5 | 126.6 | 126 | 124.7 | 124.7 | 126.6 | 126.9 | 126.5 | 127.5 | 128.7 | 129.1 | 129 |  | 129.6 | 123.7
SUI 132KV | 132.2 | 132.4 | 130.4 | 132 | 132 | 132 | 130.9 | 130.9 | 129 | 130.7 | 127.8 | 126.3 | 128.7 | 128.2 | 128 | 127 | 127.1 | 127.6 | 126.6 | 127.3 | 128.7 | 128.6 | 127.4 | 126.8 | 128.4 | 128.4 | 128.9 | 130.1 | 131.4 | 131.9 | 132.2 |  | 132.4 | 126.3
DUBI 132KV | 129 | 129.3 | 129.8 | 128.6 | 128.6 | 128.6 | 129 | 129 | 126 | 128.9 | 128.8 | 125.7 | 127.5 | 127.8 | 128.7 | 126.9 | 123.4 | 123.2 | 129 | 126.8 | 127.2 | 129.4 | 126.8 | 123 | 129.5 | 128.4 | 131.2 | 128.4 | 127.3 | 128.5 | 129.5 |  | 131.2 | 123
ANAMANI 132KV | 132.4 | 132.8 | 131.4 | 129.6 | 129.6 | 129.6 | 130.2 | 130.2 | 127 | 128.5 | 127.2 | 124.6 | 125.7 | 126.9 | 127.6 | 127.5 | 125.3 | 123.7 | 128 | 126.7 | 125.8 | 129 | 126.1 | 121.1 | 127.9 | 128.3 | 131.8 | 129.8 | 129.4 | 130.7 | 132.3 |  | 132.8 | 121.1
KG-A 132KV | 134.9 | 132.4 | 129.8 | 134.8 | 134.8 | 134.8 | 132.5 | 132.5 | 134 | 134.9 | 132.2 | 131.4 | 134.1 | 133.7 | 132.1 | 131.4 | 132 | 130.9 | 134.6 | 134.7 | 134.9 | 134.7 | 131.7 | 130.2 | 136.8 | 136.9 | 135.3 | 136.3 | 135.88 | 132.6 | 130.7 |  | 136.9 | 129.8
KOHALPUR 132KV | 131.6 | 136.7 | 139 | 134 | 134 | 134 | 136 | 136 | 124.4 | 132 | 129.85 | 127.1 | 127.7 | 131.2 | 126.2 | 131.6 | 129.9 | 126.6 | 126.7 | 127.1 | 126.8 | 129.7 | 131.9 | 133.1 | 131.2 | 132.7 | 132.7 | 133.8 | 133.9 | 134.4 | 133.7 |  | 139 | 124.4
SUI 66KV | 66.7 | 66.6 | 65.9 | 66.7 | 66.7 | 66.7 | 66 | 66 | 64.8 | 65.5 | 63.9 | 63.2 | 64.4 | 64 | 64 | 63.3 | 63.7 | 63.8 | 63.4 | 63.8 | 64.4 | 64.5 | 64 | 63.7 | 64.6 | 64.4 | 64.6 | 65.1 | 66 | 66.2 | 66.5 |  | 66.7 | 63.2
[33 empty] | 0 | 0
Kathmandu Load | 142.905 | 139.204 | 130.999 | 134.84 | 132.84 | 158.44 | 199.14 | 269.64 | 298.74 | 342.44 | 365.48 | 371.04 | 346.328 | 335.26 | 42 | 315.48 | 301.416 | 296.64 | 288.84 | 288.44 | 283.44 | 291.06 | 305.24 | 376 | 393.8 | 371.14 | 334.12 | 302.48 | 280.78 | 223.22 | 166.26 |  | 393.8 | 42
MRS-SYU | 6.1 | 4.4 | -1.1 | -1.5 | -2.6 | 5 | 13 | 18.5 | 40.1 | 36 | 44.2 | 34.8 | 38.8 | 33 | 28.7 | 28.3 | 17.5 | 15.6 | 19 | 17.3 | 15 | 11.7 | 18.9 | 36 | 37.1 | 35.2 | 30.6 | 31.6 | 34.4 | 24.8 | -2.4 | 75 | 44.2 | -2.6
NMRS-MATA | 7.2 | 4.6 | -2.6 | -2.7 | -4.4 | 4.5 | 15.5 | 20.9 | 48.5 | 49.5 | 60.4 | 47.9 | 52.2 | 44.9 | 39.7 | 33.8 | 19.4 | 16.9 | 23 | 21.4 | 23.4 | 19 | 31.3 | 49 | 49.3 | 46.7 | 41.1 | 42.5 | 44.5 | 28.8 | -5.5 | 240 | 60.4 | -5.5
KL2-MATA | -43 | -45.5 | -45.5 | -42.1 | -46 | -44 | -34.5 | 19 | -11 | 10.1 | 16 | 26.3 | 18.6 | 25.7 | 20.8 | 17.4 | 12.5 | 13.1 | 12 | 17 | 25 | 33 | 32 | 36 | 42 | 35 | 24 | 17 | 9 | -5 | -10.6 | 240 | 42 | -46
KL1-SYU | -6.2 | -1.5 | -10.2 | -6.9 | -8.2 | -6.1 | 1.1 | 3 | 7.9 | 23.6 | 26.6 | 23.8 | 22.1 | 22.8 | 20.9 | 9.1 | 5.9 | 7.4 | 4 | 9 | 7 | 10 | 8.4 | 13 | 28.2 | 14 | 9.7 | 9.7 | 11.2 | 1.5 | -4 | 60 | 28.2 | -10.2
KHIMTI-LAMOSANGHU | 82.665 | 82.164 | 96.359 | 94 | 100 | 105 | 110 | 115 | 120 | 130 | 126 | 145.96 | 109.388 | 103.32 | 104.96 | 116.44 | 138.876 | 140 | 131.2 | 129.6 | 121.6 | 129.92 | 128 | 148.8 | 144 | 153.6 | 142.08 | 115.04 | 95.04 | 79.68 | 92.32 | 120 | 153.6 | 79.68
LAMOSHANGU-BHAKTAPUR | 66.6 | 68.2 | 73.6 | 70.5 | 76.9 | 76.4 | 74.8 | 79.8 | 82.8 | 85.9 | 86.1 | 93.1 | 77.4 | 74.1 | 74.4 | 80.8 | 91.1 | 86.3 | 90 | 89.1 | 85 | 91 | 89 | 99 | 98 | 102 | 95.2 | 81.5 | 71.9 | 94.4 | 71
BALAJU-SYUCHATAR | 49.1 | 55.4 | 64.7 | 62 | 69.5 | 58.4 | 40.6 | 31.6 | -0.9 | -17.9 | -30.3 | -15.2 | -21.6 | -19.2 | -7.9 | 7.7 | 33.2 | 32.3 | 27 | 27 | 12 | 15.1 | -0.6 | -15 | -22 | -12 | -2.2 | -10.1 | -13.5 | 5.9 | 46.6
DHALKE-NAWALPUR I | 77.8 | 80 | 94.7 | 93.8 | 101 | 100 | 93.8 | 94.4 | 92.7 | 81.1 | 67.8 | 77.6 | 60.6 | 73.2 | 72.2 | 69.3 | 86.7 | 79.7 | 86 | 81 | 83 | 94 | 97 | 95 | 88 | 89 | 81.6 | 68.7 | 105.7 | 59 | 73.3 |  | 105.7 | 59
N. BHARATPUR-BARDGHAT I | 7.7 | 11.5 | 15.9 | 16.7 | 12.9 | 8.6 | 1.9 | 0 | -14.5 | -8.9 | -17.5 | -8.3 | -8.6 | -4.3 | -1.9 | -5 | 6.6 | 6 | -6.3 | -5.4 | 2 | 2.3 | -2.4 | -4.6 | -6.4 | -4.2 | -2.4 | -3 | -5.8 | 3.3 | 14.3 |  | 16.7 | -17.5
DAMAK-DUHABI | -11.6 | -10.2 | -7.9 | -6.7 | -6.6 | -13.6 | -18.7 | -26.3 | -37.1 | -41.9 | -47.7 | -42.8 | -38.3 | -28.5 | -27.6 | -21.6 | -20.1 | -21.1 | -29 | -27.3 | -38 | -35 | -50 | -59.2 | -52 | -45 | -38.3 | -33.5 | -27.4 | -18.3 | -14 |  | -6.6 | -59.2
HETAUDA-KAMANE | 16.3 | 17.3 | 9 | 12.1 | 16.7 | 15.2 | 18.2 | 6.3 | 13.1 | -1.8 | -2.5 | -8 | 0 | -10.4 | -9.6 | 19.6 | 31.3 | 29.6 | 32 | 31 | -29 | -38 | -33.3 | -27.5 | -24 | -25 | -17.6 | -11.1 | 0 | -5.3 | -18 |  | 32 | -38
MIRCHAIYA LAHAN 2 | 92.1 | 95.3 | 87.1 | 87.1 | 82.2 | 96.3 | 94.1 | 104 | 103.7 | 103.7 | 107.6 | 100.2 | 96.1 | 91.2 | 92.2 | 108.1 | 108.1 | 111 | 109 | 112 | 111 | 92 | 105.3 | 124 | 110 | 107 | 99.6 | 108.3 | 111.7 | 105.7 | 99.7 |  | 124 | 82.2
Water Level
UTK | 1985.19 | 1985.39 | 1985.6 | 1985.8 | 1985.98 | 1986.15 |  | 1986.28 |  | 1986.15 |  | 1985.4 | 1984.3 | 1983.92 | 1984.02 | 1984.22 | 1984.42 | 1984.6 | 1984.79 | 1984.95 | 1985.15 | 1985.25 | 1985.35 |  | 1985.15 |  | 1984.45 |  | 1984.02 | 1984.14 | 1984.4
KGA | 521.3 | 521.64 | 521.98 | 522.32 | 522.66 | 523.03 |  | 523.16 |  | 523 |  | 522.68 | 522.98 | 522.68 | 522.8 | 522.86 | 522.82 | 522.9 | 523.01 | 522.86 | 522.71 |  | 522.64 |  | 522.15 |  | 521.7 |  | 521.3 | 521 | 521.2
MMRS | 623.4 | 623.41 | 623.41 | 623.44 | 623.43 | 623.44 |  | 623.41 |  | 623.4 |  | 623.39 | 623.35 | 623.29 | 623.22 | 623.25 | 623.09 | 623.003 | 623.04 | 622.94 | 622.8 |  | 622.69 |  | 622.59 |  | 622.52 |  | 622.34 | 622.25 | 622.08
MRS | 334.89 | 335.1 | 335.46 | 335.92 | 336.22 | 336.52 |  | 336.64 |  | 336.5 |  | 336.34 | 336.19 | 336.14 | 336.15 | 336.18 | 336.21 | 336.24 | 336.42 | 336.77 | 337.04 | 337.19 | 337.31 |  | 337.28 |  | 337.03 |  | 336.75 | 336.44 | 336.22
CHM | 885.6 | 886.3 | 886.8 | 887.2 | 887.5 | 887.4 |  | 887.5 |  | 887.5 |  | 887.2 | 886.8 | 886.8 | 886.8 | 886.7 | 886.5 | 886.5 | 886.5 | 886.5 | 886.4 |  | 886.3 |  | 885.4 |  | 884.9 |  | 884.8 | 884.8 | 884.8
KL 1 | 0: 1519.7; 0.125: 1519.71; 0.58333: 1519.73
Others IPP Detail
Upper Mai Khola(9.98) | 0.125: 0.2; 0.16667: 0.18; 0.20833: 0.17 | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0.2 | 0.18 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1674.73; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/21)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 22
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/22 |  |  | 2080/10/22 |  |  | Tuesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 635.1 | 591.7 | 592.4 | 568 | 506.5 | 563.1 | 580.4 | 532.4 | 536.7 | 378.2 | 157.4 | 145.5 | 507.7 | 663.2 | 679.2 | 730.5 | 737.1 | 737.2 | 735.7 | 614.1 | 619.7 | 586.6 | 521.3 | 455.3 | 335.3 | 352.1 | 348.1 | 509.9 | 609.4 | 698.6 | 621.9
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1695MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1186 | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1299.59 | 1361.19 | 1494.99 | 1591.69 | 1695.09 | 1648.79 | 1544.89 | 1436.09 | 1373.09 | 1373.39 | 1400.29 | 1433.89 | 1443.29 | 1471.79 | 1301.89 | 1306.49 | 1320.09 | 1807.02 | 1741.79 | 1704.59 | 1610.89 | 1487.09 | 1502.89 | 1333.39 | 1326.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1648.79 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1648.79 MW
Solu Khola Dudhkoshi(86) | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 27.2 | 27.3 | 27.2 | 25 | 25.2 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 25.8 | 86 | 30.4 | 25
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 22
Super Dordi (54) | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 9.7 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/22)
Likhu-IV(52.4) | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 52.4 | 14 | 12.1
Upper Marsyangdi "A"(50) | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 50 | 25.5 | 25.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 45 | 15.4 | 14 |  | IPP | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 463.25 | 463.35 | 463.25 | 461.05
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 41.2 | 41.2 | 41.2 | 41.1 | 38.2 | 38.1 | 38.2 | 143.2 | 443.2 | 432.2 | 37.2 | 37.2
Mistri Khola(42) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42 | 6.6 | 6 |  | NEA ROR PROR | 110.94 | 110.94 | 111.74 | 106.14 | 115.84 | 197.44 | 278.54 | 297.74 | 334.94 | 253.84 | 227.94 | 211.64
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 621.9 | 635.1 | 591.7 | 592.4 | 568 | 506.5 | 580.4 | 536.7 | 157.4 | 145.5 | 507.7 | 663.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 250 | 250 | 200 | 0
Nyadi(30) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 30 | 7.2 | 7 |  | System_Load | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1361.19 | 1591.69 | 1648.79 | 1544.89 | 1436.09 | 1373.09
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 28 | 6.8 | 6.7 |  | National_Load | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1361.19 | 1591.69 | 1648.79 | 1544.89 | 1436.09 | 1373.09
Dordi(27) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 30 | 6.1 | 5.4
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 8.3 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 25 | 6.8 | 6.8
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 9.3 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 17 | 17 | 17 | 21 | 22.1 | 22.4 | 21.4 | 20.6 | 18.8 | 18.7 | 18 | 17.6 | 19.7 | 22.2 | 19 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 16 | 16 | 16 | 18.7 | 18.7 | 240 | 22.4 | 16
Total IPP | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 464.05 | 463.25 | 463.35 | 463.25 | 461.05 | 461.25 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 461.85 | 1042.4 | 464.05 | 461.05
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 105 | 225 | 405 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 15 | 0 | 210 | 220 | 320 | 280 | 180 | 130 | 20 | 0 | 456 | 405 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 14.2 | 14.2 | 14.2 | 14.1 | 11.2 | 11.1 | 11.2 | 11.2 | 11.1 | 11.2 | 11.2 | 11.2 | 10.2 | 10.2 | 10.2 | 10.2 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 13.1 | 13.1 | 13.1 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 22.1 | 14.2 | 7
Total NEA SUBSIDIARIES | 41.2 | 41.2 | 41.2 | 41.1 | 38.2 | 38.1 | 38.2 | 38.2 | 188.1 | 143.2 | 263.2 | 443.2 | 432.2 | 37.2 | 37.2 | 37.2 | 34 | 34 | 34 | 69 | 49 | 49 | 34 | 250.1 | 260.1 | 360.1 | 316.5 | 216.5 | 166.5 | 56.5 | 36.5 | 538.1 | 443.2 | 34
KGA(144) | 0 | 0 | 0 | 0 | 0 | 32.8 | 61.8 | 81.8 | 97.3 | 101.2 | 129.1 | 129.9 | 59.4 | 61.4 | 61.6 | 45.1 | 28.4 | 48.3 | 48.3 | 48.8 | 30.1 | 30.1 | 71.9 | 139.6 | 139.7 | 139.7 | 110.7 | 91 | 91 | 60 | 0 | 144 | 139.7 | 0
Middle MRS(70) | 23.9 | 23.9 | 24.7 | 24.8 | 0 | 34.5 | 25 | 34.7 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 25 | 24 | 24.7 | 24.8 | 24.9 | 30.9 | 35.4 | 24.8 | 24.8 | 25.3 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 24.8 | 70 | 35.4 | 0
MRS(69) | 0 | 0 | 0 | 0 | 31.8 | 46.1 | 52.7 | 68 | 70.8 | 52.5 | 68.1 | 68.5 | 54.5 | 32.5 | 17 | 16.1 | 10.1 | 17.1 | 23.4 | 23.2 | 33.6 | 33.6 | 53.1 | 64.1 | 69.3 | 69.3 | 51.4 | 51.3 | 51.3 | 33 | 22.4 | 69 | 70.8 | 0
U Trisuli 3A(60) | 43.3 | 43.3 | 43.3 | 37.6 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 36 | 36 | 35.8 | 38 | 38 | 38 | 38 | 37 | 35.3 | 35.3 | 35.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 31 | 31 | 35 | 35 | 39.3 | 60 | 43.3 | 31
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10.7 | 10 | 23.5 | 28.6 | 25 | 15.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10 | 14.2 | 14.2 | 10.4 | 9.9 | 9.9 | 10.3 | 26.8 | 27.3 | 27 | 9.7 | 9.7 | 9.7 | 0 | 0 | 30 | 28.6 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 2.9 | 7.1 | 13.3 | 17.2 | 17.2 | 18 | 19.9 | 17.4 | 14.4 | 8.4 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19.9 | 0 | [14 empty] | Tanakpur | 67 | 67.7 | 64 | 59.4 | 60 | 61 | 65.4 | 59.6 | 59.9 | 64.2 | 50.1 | 53.1 | 51.6 | 64.9 | 70.5 | 69.9 | 44.1 | 44.4 | 73.3 | 67.7 | 63.2 | 58 | 71.9 | 53.4
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 15 | 4.5 | 4.5 | [14 empty] | Muz | 412 | 354.5 | 418.8 | 399 | 442.5 | 445.8 | 357 | 6.5 | 1.9 | 358.1 | 460 | 451.1 | 475.9 | 488.6 | 488.3 | 480.9 | 420.5 | 466.6 | 296 | 200 | 370 | 391 | 413 | 412.1
DEVI(14.1) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 14.1 | 11.2 | 11.2 | [14 empty] | Ram | 3 | 19 | 3.6 | 3.6 | 4 | 27.9 | 43.1 | 30.5 | 26.4 | 23.9 | 13.1 | 15 | 23 | -1 | 0 | 0 | 2.8 | 3.7 | 6.3 | 5 | 4.2 | 4 | 27.8 | 2.7
MODI(14) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 14 | 3.3 | 2.9 | [14 empty] | Rax | 104 | 109.4 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 98 | 102 | 104 | 103 | 109.6 | 70.6 | 0 | 0 | 0 | 0 | 87 | 112.6 | 104
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 50 | 41.1 | 0 | 0 | 0 | 45.7 | 71.2 | 60.8 | 57.3 | 61.5 | 70 | 62 | 78 | 79.6 | 75.4 | 75.3 | 76.1 | 71.9 | 79.7 | 79.4 | 72.5 | 69.4 | 73.3 | 49.7
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 67 | 67.7 | 64 | 59.4 | 60 | 61 | 65.4 | 59.6 | 59.9 | 64.2 | 50.1 | 53.1 | 51.6 | 64.9 | 70.5 | 69.9 | 44.1 | 44.4 | 73.3 | 67.7 | 63.2 | 58 | 71.9 | 53.4
Total ROR | 110.94 | 110.94 | 111.74 | 106.14 | 115.84 | 197.44 | 234.24 | 278.54 | 310.44 | 297.74 | 339.64 | 334.94 | 253.84 | 227.94 | 211.64 | 195.74 | 173.94 | 200.94 | 210.24 | 205.24 | 176.94 | 175.94 | 237.64 | 341.84 | 347.64 | 347.34 | 280.44 | 260.64 | 264.64 | 205.64 | 129.84 | 489.91 | 347.64 | 106.14 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.77083: 19.82; 0.79167: 10.6; 0.8125: 0 | 60 | 19.82 | 0 | [15 empty] | 412 | 354.5 | 418.8 | 399 | 442.5 | 445.8 | 357 | 6.5 | 1.9 | 358.1 | 460 | 451.1 | 475.9 | 488.6 | 488.3 | 480.9 | 420.5 | 466.6 | 296 | 200 | 370 | 391 | 413 | 412.1
KL2(32) | 0.77083: 8.95; 0.79167: 4.6; 0.8125: 0 | 32 | 8.95 | 0 | [15 empty] | 3 | 19 | 3.6 | 3.6 | 4 | 27.9 | 43.1 | 30.5 | 26.4 | 23.9 | 13.1 | 15 | 23 | -1 | 0 | 0 | 2.8 | 3.7 | 6.3 | 5 | 4.2 | 4 | 27.8 | 2.7
KL3(14) | 0.77083: 3.16; 0.79167: 1.7; 0.8125: 0 | 14 | 3.16 | 0 | [15 empty] | 104 | 109.4 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 98 | 102 | 104 | 103 | 109.6 | 70.6 | 0 | 0 | 0 | 0 | 87 | 112.6 | 104
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.93 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 31.93 | 0 | [15 empty] | 50 | 41.1 | 0 | 0 | 0 | 45.7 | 71.2 | 60.8 | 57.3 | 61.5 | 70 | 62 | 78 | 79.6 | 75.4 | 75.3 | 76.1 | 71.9 | 79.7 | 79.4 | 72.5 | 69.4 | 73.3 | 49.7
TANAKPUR | 53.4 | 66.6 | 67.7 | 64 | 59.4 | 60 | 61.6 | 61 | 65.4 | 65.4 | 63.9 | 59.6 | 59.9 | 64.2 | 50.1 | 53.1 | 51.6 | 64.9 | 70.5 | 69.9 | 44.1 | 60.3 | 44.4 | 73.5 | 73.3 | 65 | 67.7 | 62.8 | 63.2 | 58 | 71.9 |  | 73.5 | 44.1
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 412.1 | 412.1 | 354.5 | 418.8 | 399 | 442.5 | 436.5 | 445.8 | 347 | 357 | 208.7 | 6.5 | 1.9 | 358.1 | 460 | 451.1 | 475.9 | 488.6 | 488.3 | 480.9 | 420.5 | 486.6 | 466.6 | 360.7 | 296 | 185.8 | 200 | 205 | 370 | 391 | 413 |  | 488.6 | 1.9
RAMNAGAR | 2.7 | 2.7 | 19 | 3.6 | 3.6 | 4 | 23.5 | 27.9 | 45.3 | 43.1 | 37.6 | 30.5 | 26.4 | 23.9 | 13.1 | 15 | 23 | -1 | 0 | 0 | 2.8 | 3.4 | 3.7 | 6.2 | 6.3 | 5.6 | 5 | 5 | 4.2 | 4 | 27.8 |  | 45.3 | -1 | [22 empty] | 67 | 0 | 412 | 3 | 104 | 50
RAXAUL 132 | 104 | 104 | 109.4 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 98 | 102 | 104 | 103 | 109.6 | 70.6 | 0 | 0 | 0 | 0 | 0 |  |  |  | 87 | 112.6 |  | 112.6 | 0 | [22 empty] | 67.7 | 0 | 354.5 | 19 | 109.4 | 41.1
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 64 | 0 | 418.8 | 3.6 | 106 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 59.4 | 0 | 399 | 3.6 | 106 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 60 | 0 | 442.5 | 4 | 0 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 61 | 0 | 445.8 | 27.9 | 0 | 45.7
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 65.4 | 0 | 357 | 43.1 | 0 | 71.2
SAMPATIYA 132 kV | 49.7 | 49.7 | 41.1 | 0 | 0 | 0 | 41.5 | 45.7 | 74.7 | 71.2 | 68 | 60.8 | 57.3 | 61.5 | 70 | 62 | 78 | 79.6 | 75.4 | 75.3 | 76.1 | 69.4 | 71.9 | 80.9 | 79.7 | 78.9 | 79.4 | 75.3 | 72.5 | 69.4 | 73.3 |  | 80.9 | 0 | [22 empty] | 59.6 | 0 | 6.5 | 30.5 | 0 | 60.8
Total IMPORT | 621.9 | 635.1 | 591.7 | 592.4 | 568 | 506.5 | 563.1 | 580.4 | 532.4 | 536.7 | 378.2 | 157.4 | 145.5 | 507.7 | 663.2 | 679.2 | 730.5 | 737.1 | 737.2 | 735.7 | 614.1 | 619.7 | 586.6 | 521.3 | 455.3 | 335.3 | 352.1 | 348.1 | 509.9 | 609.4 | 698.6 | 0 | 737.2 | 145.5 | [22 empty] | 59.9 | 0 | 1.9 | 26.4 | 0 | 57.3
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 64.2 | 0 | 358.1 | 23.9 | 0 | 61.5
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 50.1 | 0 | 460 | 13.1 | 70 | 70
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 53.1 | 0 | 451.1 | 15 | 98 | 62
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 51.6 | 0 | 475.9 | 23 | 102 | 78
TOTAL SYSTEM LOAD (ACTUAL) | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1299.59 | 1361.19 | 1494.99 | 1441.69 | 1445.09 | 1398.79 | 1294.89 | 1236.09 | 1373.09 | 1373.39 | 1400.29 | 1433.89 | 1443.29 | 1471.79 | 1301.89 | 1306.49 | 1320.09 | 1607.02 | 1541.79 | 1504.59 | 1410.89 | 1287.09 | 1402.89 | 1333.39 | 1326.79 | 2231.81 | 1607.02 | 1186.09 | [22 empty] | 64.9 | 0 | 488.6 | -1 | 104 | 79.6
Interruption/Tripping | 0.29167: 150; 0.3125: 250; 0.33333: 250; 0.375: 250; 0.41667: 200; 0.77083: 200; 0.79167: 200; 0.8125: 200; 0.83333: 200; 0.85417: 200; 0.875: 100 |  | 250 | 100 | [22 empty] | 70.5 | 0 | 488.3 | 0 | 103 | 75.4
TOTAL SYSTEM LOAD (EXPECTED) | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1299.59 | 1361.19 | 1494.99 | 1591.69 | 1695.09 | 1648.79 | 1544.89 | 1436.09 | 1373.09 | 1373.39 | 1400.29 | 1433.89 | 1443.29 | 1471.79 | 1301.89 | 1306.49 | 1320.09 | 1807.02 | 1741.79 | 1704.59 | 1610.89 | 1487.09 | 1502.89 | 1333.39 | 1326.79 | 1693.71 | 1807.02 | 1186.09 | [22 empty] | 69.9 | 0 | 480.9 | 0 | 109.6 | 75.3
TOTAL NATIONAL LOAD (ACTUAL) | 1238.09 | 1251.29 | 1208.69 | 1203.69 | 1186.09 | 1206.09 | 1299.59 | 1361.19 | 1494.99 | 1591.69 | 1695.09 | 1648.79 | 1544.89 | 1436.09 | 1373.09 | 1373.39 | 1400.29 | 1433.89 | 1443.29 | 1471.79 | 1301.89 | 1306.49 | 1320.09 | 1807.02 | 1741.79 | 1704.59 | 1610.89 | 1487.09 | 1502.89 | 1333.39 | 1326.79 |  | 1807.02 | 1186.09 | [22 empty] | 44.1 | 0 | 420.5 | 2.8 | 70.6 | 76.1
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 44.4 | 0 | 466.6 | 3.7 | 0 | 71.9
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 73.3 | 0 | 296 | 6.3 | 0 | 79.7
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67.7 | 0 | 200 | 5 | 0 | 79.4
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 63.2 | 0 | 370 | 4.2 | 0 | 72.5
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58 | 0 | 391 | 4 | 87 | 69.4
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 71.9 | 0 | 413 | 27.8 | 112.6 | 73.3
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 53.4 | 0 | 412.1 | 2.7 | 104 | 49.7
NET IMPORT | 621.9 | 635.1 | 591.7 | 592.4 | 568 | 506.5 | 563.1 | 580.4 | 532.4 | 536.7 | 378.2 | 157.4 | 145.5 | 507.7 | 663.2 | 679.2 | 730.5 | 737.1 | 737.2 | 735.7 | 614.1 | 619.7 | 586.6 | 521.3 | 455.3 | 335.3 | 352.1 | 348.1 | 509.9 | 609.4 | 698.6 |  | 737.2 | 145.5
HZ | 50.03 | 50.04 | 50 | 50.015 | 49.955 | 50.029 | 49.898 | 50.046 | 50.081 | 50 | 49.935 | 50.113 | 50.015 | 50.067 | 50.103 | 50.046 | 49.924 | 50 | 49.93 | 49.98 | 50.04 | 50.09 | 49.98 | 49.96 | 50.01 | 49.91 | 50.066 | 50.008 | 50.085 | 49.982 | 49.852 |  | 50.113 | 49.852
HTD 132KV | 128.3 | 128.3 | 128.3 | 128.3 | 129.7 | 125.8 | 126.1 | 125.8 | 123.8 | 128.5 | 126.6 | 126.6 | 127.4 | 127.6 | 124.7 | 124.2 | 124.6 | 122.5 | 122.7 | 123.5 | 128.6 | 126 | 126.8 | 124.4 | 126.8 | 126.8 | 128.3 | 127.8 | 125.2 | 130 | 128.5 |  | 130 | 122.5
SUI 132KV | 131.8 | 131.8 | 131.8 | 131.6 | 132.7 | 130.4 | 130.5 | 129.9 | 128.1 | 130.1 | 128.1 | 128.1 | 129.2 | 129.7 | 127.5 | 127.2 | 127.4 | 125.8 | 126 | 126.6 | 131.1 | 128.9 | 129.8 | 127.1 | 128.9 | 128.9 | 131.1 | 130.9 | 129.3 | 133.3 | 132.4 |  | 133.3 | 125.8
DUBI 132KV | 128.9 | 128.9 | 128.9 | 128.8 | 132.8 | 126.8 | 126.3 | 128.3 | 128.4 | 129.7 | 125.8 | 125.8 | 127.5 | 128.3 | 123.9 | 130.2 | 127.3 | 124 | 126 | 128.3 | 130 | 130.6 | 128.8 | 128.4 | 129.6 | 129.6 | 130 | 128.8 | 131 | 128 | 128.1 |  | 132.8 | 123.9
ANAMANI 132KV | 132.8 | 132.8 | 132.8 | 130.4 | 134 | 129.4 | 128.4 | 130.8 | 128.9 | 129 | 125.7 | 125.7 | 124.9 | 127.3 | 124.1 | 129 | 129.2 | 125.3 | 125.3 | 128.8 | 128.7 | 128.2 | 126.9 | 125.2 | 127.6 | 127.6 | 131.4 | 130 | 132.4 | 130.5 | 130.7 |  | 134 | 124.1
KG-A 132KV | 130.5 | 130.5 | 130.5 | 130.9 | 130.9 | 131.2 | 134.9 | 135 | 134.1 | 137.2 | 135 | 135 | 135.8 | 135.8 | 131.4 | 130.7 | 133.6 | 131.5 | 131.1 | 133 | 135.4 | 134.9 | 134.6 | 135.3 | 135.8 | 135.8 | 138.6 | 138.5 | 135 | 133.7 | 130.1 |  | 138.6 | 130.1
KOHALPUR 132KV | 133.8 | 133.8 | 133.8 | 132.9 | 134.8 | 129.2 | 129.9 | 133.5 | 129.8 | 131.1 | 130.9 | 130.9 | 132.3 | 131.8 | 130.9 | 135.1 | 132 | 132 | 132 | 122.8 | 137.6 | 135.4 | 137.8 | 125.6 | 129.2 | 129.2 | 135.7 | 135.5 | 133.3 | 130 | 130.7 |  | 137.8 | 122.8
SUI 66KV | 66.1 | 66.1 | 66.1 | 66.4 | 66.7 | 65.5 | 65.6 | 65.2 | 64.4 | 65.1 | 63.9 | 64.4 | 64.8 | 65.2 | 63.9 | 63.9 | 64 | 64 | 63.2 | 63.7 | 64.6 | 64.7 | 65.2 | 64.4 | 64.9 | 64.9 | 65.8 | 65.6 | 65.2 | 67 | 66.7 |  | 67 | 63.2
[33 empty] | 0 | 0
Kathmandu Load | 150.1 | 140.56 | 134.38 | 126.131 | 125.931 | 141.605 | 181.5 | 212.138 | 280.626 | 340.575 | 364.815 | 369.44 | 336.74 | 322.26 | 42 | 290 | 291.612 | 281.1 | 285.56 | 293.34 | 285.68 | 294.3 | 313.88 | 396.5 | 400.72 | 381.2 | 339.6 | 316.08 | 285.86 | 201.74 | 173.2 |  | 400.72 | 42
MRS-SYU | -11.1 | -4.7 | -4.5 | -20.3 | -20.8 | -3.8 | 12.9 | 19.7 | 37.2 | 38.6 | 47.3 | 50.8 | 39.2 | 34.7 | 12.6 | 12.6 | 5 | 4.5 | 7.5 | 6.9 | 10.1 | 11.4 | 27.8 | 38.2 | 38.7 | 42.5 | 34.5 | 29.2 | 35 | 8.5 | 3.7 | 75 | 50.8 | -20.8
NMRS-MATA | -17.7 | -9.9 | -9.1 | -29.8 | -28.5 | -1.5 | 19.5 | 28.6 | 51.1 | 51.5 | 62.4 | 66.9 | 52.8 | 47.2 | 19.3 | 15.2 | 3.4 | 3.1 | 7.3 | 6.4 | 11.7 | 13.9 | 35.7 | 48.2 | 48.4 | 53.8 | 44.5 | 37.9 | 40 | 3.1 | -1.1 | 240 | 66.9 | -29.8
KL2-MATA | -12.4 | -16.5 | -20 | -14.1 | -15.4 | -44 | -38.4 | -31.8 | -20.5 | 18.9 | 22.5 | 15.9 | 9.3 | 20 | 20.6 | 13.9 | 17.7 | 15 | 16 | 18.7 | 38 | 29 | 25 | 42 | 47 | 34 | 22 | 18 | -6 | 0 | -7 | 240 | 47 | -44
KL1-SYU | -5.3 | -7.5 | -5.9 | -7.5 | -9.9 | -9.3 | -7 | -3.1 | 1.7 | 20.1 | 22.4 | 19.6 | 16 | 16.7 | 7 | 1.2 | 4.3 | -0.5 | 0.2 | 5.1 | 17.9 | 16.7 | 20.5 | 26.1 | 37.9 | 25.7 | 21.3 | 18 | 5 | 4.2 | 0 | 60 | 37.9 | -9.9
KHIMTI-LAMOSANGHU | 100.16 | 82.72 | 77.44 | 107.091 | 107.091 | 106.765 | 101.06 | 105.298 | 117.686 | 121.435 | 118.175 | 120 | 114.8 | 95.12 | 137.76 | 137.76 | 150.972 | 152.96 | 151.52 | 159.2 | 119.84 | 136.16 | 118.24 | 155.36 | 142.08 | 138.56 | 132.96 | 128.64 | 123.52 | 97.6 | 84.96 | 120 | 159.2 | 77.44
LAMOSHANGU-BHAKTAPUR | 73.6 | 64.2 | 62.4 | 78.3 | 77.8 | 78 | 74.7 | 77.1 | 81.1 | 83.9 | 81.6 | 79.3 | 78.7 | 68.5 | 90.7 | 87 | 96.5 | 98.2 | 98 | 102 | 82.7 | 91 | 82.9 | 100.8 | 93.9 | 92 | 90.1 | 89.5 | 87 | 73 | 68
BALAJU-SYUCHATAR | 62.1 | 50.9 | 52 | 78.6 | 69.1 | 63.6 | 36.9 | 26.9 | 0.5 | -19.9 | 32.4 | -33.1 | -15.8 | -17 | 23 | 29.5 | 44.4 | 50.5 | 41.7 | 46.6 | 12.6 | 20.7 | -5.4 | -16.7 | -25 | -21.6 | -6.2 | 0.7 | 17 | 33.1 | 39
DHALKE-NAWALPUR I | 80.98 | 66.9 | 63.1 | 85.9 | 91.9 | 106.3 | 93.4 | 98.7 | 96.1 | 79.4 | 74.2 | 58.1 | 58.5 | 71.6 | 82.3 | 83.6 | 95.8 | 97.1 | 95.5 | 95.1 | 80.9 | 104 | 88.7 | 98.6 | 88.7 | 83 | 88 | 91.2 | 103 | 71 | 75 |  | 106.3 | 58.1
N. BHARATPUR-BARDGHAT I | 24.5 | 16.3 | 15.2 | 36.8 | 28.7 | 27.1 | 1.7 | 0 | -17.3 | -10.9 | -20 | -24 | -13.2 | -16.1 | -4.2 | -5.2 | 2.5 | 7.9 | 4.9 | 10 | 14.3 | 8.8 | -3.6 | -14.4 | -11.7 | -13.2 | -11.6 | -6.2 | -6 | 12.7 | 14.2 |  | 36.8 | -24
DAMAK-DUHABI | -12.4 | -11.5 | -10.4 | -9.3 | -10.1 | -11.8 | -19 | -25.6 | -39.4 | -43.7 | -46.1 | -51.3 | -44.7 | -29.4 | -25.5 | -22.5 | -19.8 | -17.3 | -21.7 | -22 | -36.5 | -44.6 | -51.8 | -62.4 | -53.5 | -48.8 | -38.9 | -35.1 | -28 | -20 | -16 |  | -9.3 | -62.4
HETAUDA-KAMANE | -21.4 | -12.7 | -9.8 | -28.9 | -26.3 | 4.2 | 14.4 | 16.1 | 21.6 | -3.6 | 2.3 | 8.1 | 3.9 | -6.8 | 18.4 | 24.9 | 26 | 26.8 | 24.3 | 25.3 | -41.9 | -33.6 | -20.3 | -24.1 | -15.7 | -8.4 | -9.8 | -13 | 1.1 | -21 | -19 |  | 26.8 | -41.9
MIRCHAIYA LAHAN 2 | 100 | 88.8 | 90.8 | 89.9 | 77.8 | 88.2 | 90.3 | 96.4 | 112.5 | 104.4 | 107 | 110.7 | 100.5 | 89.8 | 112.1 | 98 | 95.3 | 91.4 | 101.7 | 102.1 | 94.7 | 96.3 | 102.4 | 115.1 | 103.4 | 107.9 | 104 | 107.4 | 106 | 103.1 | 101 |  | 115.1 | 77.8
Water Level
UTK | 1984.7 | 1984.9 | 1985.1 | 1985.37 | 1985.47 | 1985.68 |  | 1985.92 |  | 1985.9 |  | 1985.32 | 1984.38 | 1983.62 | 1983.85 | 1984.07 | 1984.29 | 1984.45 | 1984.65 | 1984.82 | 1984.9 |  | 1985.1 |  | 1984.9 |  | 1984.32 |  | 1983.88 | 1983.78 | 1983.98
KGA | 521.54 | 521.84 | 522.14 | 522.44 | 522.84 | 522.91 |  | 522.88 |  | 522.52 |  | 522.12 | 521.81 | 521.75 | 521.7 | 521.64 | 521.71 | 521.78 | 521.82 | 521.82 | 521.88 |  | 521.9 |  | 521.5 |  | 520.95 |  | 520.63 | 520.27 | 520.42
MMRS | 622.15 | 622.22 | 622.27 | 622.31 | 622.94 | 622.99 |  | 622.97 |  | 622.8 |  | 622.75 | 622.66 | 622.62 | 622.68 | 622.73 | 622.77 | 622.84 | 622.84 | 622.76 | 622.68 |  | 622.69 |  | 622.66 |  | 622.55 |  | 622.43 | 622.33 | 622.35
MRS | 336.48 | 336.77 | 337.01 | 337.35 | 337.43 | 337.46 |  | 337.3 |  | 336.9 |  | 336.59 | 336.27 | 336.04 | 335.94 | 335.93 | 336.11 | 336.4 | 336.55 | 336.66 | 336.6 |  | 336.52 |  | 336.25 |  | 335.87 |  | 335.67 | 335.38 | 335.38
CHM | 884.8 | 885.6 | 886.2 | 886.7 | 887.1 | 887.6 |  | 887.6 |  | 887.1 |  | 886.1 | 886 | 886 | 885.8 | 885.5 | 885.4 | 885.3 | 885.1 | 884.8 | 884.5 |  | 884.5 |  | 883.7 |  | 881.9 |  | 881.9 | 881.7 | 882.9
KL 1 | 0: 1519.75; 0.33333: 1519.76
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1695.09; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/22)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 23
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/23 |  |  | 2080/10/23 |  |  | Wednesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 624.9 | 650.8 | 643.9 | 578.8 | 590 | 646 | 620 | 637.9 | 238 | 186.4 | 163.5 | 259.6 | 572.6 | 709.5 | 69 | 624 | 705.1 | 722.7 | 765.8 | 504.2 | 674.1 | 726.3 | 659.4 | 620 | 522.1 | 512.5 | 592 | 649 | 687 | 655 | 678.4
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1705MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=330 | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1310.63 | 1358.49 | 1539.39 | 1603.99 | 1705.39 | 1650.29 | 1537.89 | 1592.69 | 1436.59 | 330.14 | 1355.59 | 1443.99 | 1469.69 | 1460.19 | 1491.99 | 1467.19 | 1455.49 | 1676.15 | 1729.85 | 1691.99 | 1642.49 | 1617.29 | 1467.49 | 1396.09 | 1294.09
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1453.99 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1453.99 MW
Solu Khola Dudhkoshi(86) | 25.8 | 25.8 | 25.8 | 24.6 | 24.6 | 24.6 | 24.6 | 25 | 25 | 25 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | s | 24.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 86 | 25.8 | 22.9
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | y | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 23
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | s | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/23)
Likhu-IV(52.4) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | t | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 52.4 | 14 | 14
Upper Marsyangdi "A"(50) | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | e | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 50 | 25.5 | 25.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | m | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 45 | 15.4 | 15.4 |  | IPP | 461.85 | 461.85 | 461.85 | 460.65 | 460.65 | 460.65 | 461.05 | 461.05 | 460.95 | 460.95 | 460.95 | 460.95
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | d | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 36.5 | 36.5 | 36.5 | 36.5 | 38.4 | 38.4 | 39.8 | 394.8 | 459.8 | 239.8 | 139.8 | 54.8
Mistri Khola(42) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | i | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42 | 6 | 6 |  | NEA ROR PROR | 107.44 | 117.64 | 82.64 | 82.64 | 82.64 | 139.64 | 237.64 | 360.14 | 316.04 | 327.54 | 219.34 | 211.34
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | s | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 678.4 | 624.9 | 650.8 | 643.9 | 578.8 | 590 | 620 | 238 | 163.5 | 259.6 | 572.6 | 709.5
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | t | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | u | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyadi(30) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | r | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 30 | 7.2 | 7.2 |  | System_Load | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1358.49 | 1453.99 | 1400.29 | 1287.89 | 1392.69 | 1436.59
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | b | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 |  | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 28 | 6.7 | 6.7 |  | National_Load | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1358.49 | 1453.99 | 1400.29 | 1287.89 | 1392.69 | 1436.59
Dordi(27) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 |  | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 30 | 5.4 | 5.4
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 |  | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 8.3 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 |  | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 25 | 6.8 | 6.8
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 |  | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 |  | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 |  | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 9.3 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 |  | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 |  | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 |  | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 |  | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 |  | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 18.7 | 18.7 | 19.5 | 20.4 | 19.7 | 19.1 | 19.3 | 19 | 19 | 19 | 19.3 | 18.7 | 18.7 | 18.7 | 18.7 |  | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 20.2 | 18.9 | 18.9 | 18.9 | 18.9 | [5 empty] | 240 | 21.6 | 18.7
Total IPP | 461.85 | 461.85 | 461.85 | 460.65 | 460.65 | 460.65 | 460.65 | 461.05 | 461.05 | 461.05 | 460.95 | 460.95 | 460.95 | 460.95 | 460.95 | 0 | 460.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 1042.4 | 461.85 | 0
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 355 | 456 | 420 | 200 | 100 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 175 | 220 | 320 | 350 | 290 | 140 | 60 | 0 | 456 | 456 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 9.5 | 9.5 | 9.5 | 9.5 | 11.4 | 11.4 | 11.34 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 16.3 | 16.3 | 9.2 | 9.2 | 9.2 | 7.6 | 7.6 | 7.6 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 22.1 | 16.3 | 7.6
Total NEA SUBSIDIARIES | 36.5 | 36.5 | 36.5 | 36.5 | 38.4 | 38.4 | 38.34 | 39.8 | 119.8 | 394.8 | 495.8 | 459.8 | 239.8 | 139.8 | 54.8 | 43.3 | 43.3 | 36.2 | 36.2 | 36.2 | 34.6 | 34.6 | 59.6 | 213.1 | 258.1 | 358.1 | 388.1 | 328.1 | 178.1 | 98.1 | 38.1 | 538.1 | 495.8 | 34.6
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 60 | 120 | 144.5 | 130 | 121.6 | 126 | 40 | 30 | 30.2 | 65 | 65.5 | 97.2 | 48.7 | 48.7 | 0 | 0 | 70.5 | 97.8 | 85.3 | 70 | 70 | 60 | 40 | 30 | 144 | 144.5 | 0
Middle MRS(70) | 24.8 | 35 | 0 | 0 | 0 | 35 | 25 | 35 | 35 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.7 | 34.8 | 24 | 24.8 | 35 | 35 | 35 | 22.6 | 34.7 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 25 | 24 | 24 | 70 | 35 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 22 | 30 | 45 | 60 | 69.4 | 60 | 56.2 | 68 | 46.8 | 48.9 | 48.5 | 34 | 39.7 | 21.9 | 21.9 | 21.9 | 0 | 0 | 55.3 | 61.5 | 46.7 | 46.7 | 32 | 15 | 16.6 | 16.6 | 69 | 69.4 | 0
U Trisuli 3A(60) | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 39.3 | 38 | 38 | 38 | 38 | 37 | 37 | 37.3 | 37.3 | 39.8 | 33.3 | 33.3 | 33.3 | 36 | 36 | 34.3 | 35.3 | 32 | 32 | 32 | 32 | 32 | 32 | 60 | 39.8 | 32
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 28.6 | 22.8 | 14.7 | 10 | 10 | 10 | 10.3 | 10.3 | 14.8 | 10.4 | 10.4 | 10.4 | 0 | 0 | 9.9 | 23.5 | 14.6 | 10 | 10 | 10 | 0 | 0 | 30 | 28.6 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 3.3 | 7.4 | 7.4 | 7.4 | 7.4 | 13.4 | 13.4 | 17.7 | 14.1 | 10 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17.7 | 0 | [14 empty] | Tanakpur | 67 | 66.1 | 59.5 | 54.6 | 60 | 60 | 63.5 | 60.7 | 59.6 | 55.7 | 69 | s | 55 | 64.7 | 68.2 | 75.6 | 61 | 67.5 | 63.4 | 68.5 | 64 | 67 | 60 | 73.2
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 15 | 4.5 | 2 | [14 empty] | Muz | 376 | 408 | 410 | 416 | 439 | 410 | 63 | 0.9 | 99 | 421 | 452 | s | 412 | 432 | 437.3 | 455.8 | 296 | 465.7 | 306.8 | 197 | 356 | 382 | 398 | 399.4
DEVI(14.1) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 14.1 | 11.2 | 9.3 | [14 empty] | Ram | 10 | 4.4 | 4.3 | 4.2 | 5 | 4 | 41 | 32.5 | 26 | 20.9 | 26.5 | t | 34 | 32.2 | 30.1 | 54 | 38.6 | 41.5 | 59 | 60 | 58 | 54 | 4 | 10
MODI(14) | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 14 | 3.5 | 2.9 | [14 empty] | Rax | 122 | 122 | 120 | 104 | 86 | 78 | 0 | 0 | 0 | 0 | 88 | e | 54 | 104 | 112.2 | 100 | 32 | 85 | 116 | 120 | 102 | 110 | 120 | 122
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 50 | 50.3 | 50.1 | 0 | 0 | 68 | 70.5 | 69.4 | 75 | 75 | 74 | u | 69 | 72.2 | 74.9 | 80.4 | 76.6 | 66.6 | 74.8 | 67 | 69 | 74 | 73 | 73.8
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 3.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.5 | [15 empty] | 67 | 66.1 | 59.5 | 54.6 | 60 | 60 | 63.5 | 60.7 | 59.6 | 55.7 | 69 | #VALUE! | 55 | 64.7 | 68.2 | 75.6 | 61 | 67.5 | 63.4 | 68.5 | 64 | 67 | 60 | 73.2
Total ROR | 107.44 | 117.64 | 82.64 | 82.64 | 82.64 | 139.64 | 165.64 | 237.64 | 320.64 | 360.14 | 332.24 | 316.04 | 327.54 | 219.34 | 211.34 | 217.84 | 227.34 | 243.74 | 251.84 | 199.24 | 194.24 | 99.54 | 110.64 | 244.7 | 292.8 | 252.84 | 232.94 | 218.24 | 181.44 | 152.04 | 142.04 | 489.91 | 360.14 | 82.64 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [15 empty] | 376 | 408 | 410 | 416 | 439 | 410 | 63 | 0.9 | 99 | 421 | 452 | #VALUE! | 412 | 432 | 437.3 | 455.8 | 296 | 465.7 | 306.8 | 197 | 356 | 382 | 398 | 399.4
KL2(32) | [31 empty] | 32 | 0 | 0 | [15 empty] | 10 | 4.4 | 4.3 | 4.2 | 5 | 4 | 41 | 32.5 | 26 | 20.9 | 26.5 | #VALUE! | 34 | 32.2 | 30.1 | 54 | 38.6 | 41.5 | 59 | 60 | 58 | 54 | 4 | 10
KL3(14) | [31 empty] | 14 | 0 | 0 | [15 empty] | 122 | 122 | 120 | 104 | 86 | 78 | 0 | 0 | 0 | 0 | 88 | #VALUE! | 54 | 104 | 112.2 | 100 | 32 | 85 | 116 | 120 | 102 | 110 | 120 | 122
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | [15 empty] | 50 | 50.3 | 50.1 | 0 | 0 | 68 | 70.5 | 69.4 | 75 | 75 | 74 | #VALUE! | 69 | 72.2 | 74.9 | 80.4 | 76.6 | 66.6 | 74.8 | 67 | 69 | 74 | 73 | 73.8
TANAKPUR | 73.2 | 67 | 66.1 | 59.5 | 54.6 | 60 | 62 | 60 | 69 | 63.5 | 63.4 | 60.7 | 59.6 | 55.7 | 69 | 69 | 55 | 64.7 | 68.2 | 75.6 | 61 | 63.9 | 67.5 | 62.5 | 63.4 | 69.5 | 68.5 | 67 | 64 | 67 | 60 |  | 75.6 | 54.6
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 399.4 | 376 | 408 | 410 | 416 | 439 | 442 | 410 | 390 | 63 | 15 | 0.9 | 99 | 421 | 452 |  | 412 | 432 | 437.3 | 455.8 | 296 | 463.5 | 465.7 | 363 | 306.8 | 204.3 | 197 | 312 | 356 | 382 | 398 |  | 465.7 | 0.9
RAMNAGAR | 10 | 9.6 | 4.4 | 4.3 | 4.2 | 5 | 4 | 4 | 28 | 41 | 38 | 32.5 | 26 | 20.9 | 26.5 |  | 34 | 32.2 | 30.1 | 54 | 38.6 | 36.5 | 41.5 | 49.2 | 59 | 60 | 60 | 58 | 58 | 54 | 4 |  | 60 | 4 | [22 empty] | 67 | 0 | 376 | 10 | 122 | 50
RAXAUL 132 | 122 | 122.2 | 122 | 120 | 104 | 86 | 78 | 78 | 78 | 0 | 0 | 0 | 0 | 0 | 88 |  | 54 | 104 | 112.2 | 100 | 32 | 45 | 85 | 114 | 116 | 120.4 | 120 | 94 | 102 | 110 | 120 |  | 122.2 | 0 | [22 empty] | 66.1 | 0 | 408 | 4.4 | 122 | 50.3
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 59.5 | 0 | 410 | 4.3 | 120 | 50.1
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 54.6 | 0 | 416 | 4.2 | 104 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 60 | 0 | 439 | 5 | 86 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 60 | 0 | 410 | 4 | 78 | 68
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 63.5 | 0 | 63 | 41 | 0 | 70.5
SAMPATIYA 132 kV | 73.8 | 50.1 | 50.3 | 50.1 | 0 |  | 60 | 68 | 72.9 | 70.5 | 70 | 69.4 | 75 | 75 | 74 |  | 69 | 72.2 | 74.9 | 80.4 | 76.6 | 65.2 | 66.6 | 70.7 | 74.8 | 67.9 | 67 | 61 | 69 | 74 | 73 |  | 80.4 | 0 | [22 empty] | 60.7 | 0 | 0.9 | 32.5 | 0 | 69.4
Total IMPORT | 678.4 | 624.9 | 650.8 | 643.9 | 578.8 | 590 | 646 | 620 | 637.9 | 238 | 186.4 | 163.5 | 259.6 | 572.6 | 709.5 | 69 | 624 | 705.1 | 722.7 | 765.8 | 504.2 | 674.1 | 726.3 | 659.4 | 620 | 522.1 | 512.5 | 592 | 649 | 687 | 655 | 0 | 765.8 | 69 | [22 empty] | 59.6 | 0 | 99 | 26 | 0 | 75
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 55.7 | 0 | 421 | 20.9 | 0 | 75
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 69 | 0 | 452 | 26.5 | 88 | 74
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | s | y | s | t | e | u
Total THERMAL | 0.29167: 150; 0.3125: 230; 0.33333: 250; 0.375: 250; 0.41667: 200; 0.75: 0 | 55.4 | 250 | 0 | [22 empty] | 55 | 0 | 412 | 34 | 54 | 69
TOTAL SYSTEM LOAD (ACTUAL) | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1310.63 | 1358.49 | 1539.39 | 1603.99 | 1705.39 | 1650.29 | 1537.89 | 1592.69 | 1436.59 | 330.14 | 1355.59 | 1443.99 | 1469.69 | 1460.19 | 1191.99 | 1267.19 | 1355.49 | 1576.15 | 1629.85 | 1591.99 | 1592.49 | 1597.29 | 1467.49 | 1396.09 | 1294.09 | 2231.81 | 1705.39 | 330.14 | [22 empty] | 64.7 | 0 | 432 | 32.2 | 104 | 72.2
Interruption/Tripping | 0.70833: 300; 0.72917: 200; 0.75: 100; 0.77083: 100; 0.79167: 100; 0.8125: 100; 0.83333: 50; 0.85417: 20; 0.875: 0; 0.91667: 0; 0.95833: 0 |  | 300 | 0 | [22 empty] | 68.2 | 0 | 437.3 | 30.1 | 112.2 | 74.9
TOTAL SYSTEM LOAD (EXPECTED) | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1310.63 | 1358.49 | 1539.39 | 1603.99 | 1705.39 | 1650.29 | 1537.89 | 1592.69 | 1436.59 | 330.14 | 1355.59 | 1443.99 | 1469.69 | 1460.19 | 1491.99 | 1467.19 | 1455.49 | 1676.15 | 1729.85 | 1691.99 | 1642.49 | 1617.29 | 1467.49 | 1396.09 | 1294.09 | 1693.71 | 1729.85 | 330.14 | [22 empty] | 75.6 | 0 | 455.8 | 54 | 100 | 80.4
TOTAL NATIONAL LOAD (ACTUAL) | 1284.19 | 1240.89 | 1231.79 | 1223.69 | 1160.49 | 1228.69 | 1310.63 | 1358.49 | 1539.39 | 1603.99 | 1705.39 | 1650.29 | 1537.89 | 1592.69 | 1436.59 | 330.14 | 1355.59 | 1443.99 | 1469.69 | 1460.19 | 1491.99 | 1467.19 | 1455.49 | 1676.15 | 1729.85 | 1691.99 | 1642.49 | 1617.29 | 1467.49 | 1396.09 | 1294.09 |  | 1729.85 | 330.14 | [22 empty] | 61 | 0 | 296 | 38.6 | 32 | 76.6
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67.5 | 0 | 465.7 | 41.5 | 85 | 66.6
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 63.4 | 0 | 306.8 | 59 | 116 | 74.8
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 68.5 | 0 | 197 | 60 | 120 | 67
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 64 | 0 | 356 | 58 | 102 | 69
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67 | 0 | 382 | 54 | 110 | 74
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 60 | 0 | 398 | 4 | 120 | 73
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 73.2 | 0 | 399.4 | 10 | 122 | 73.8
NET IMPORT | 678.4 | 624.9 | 650.8 | 643.9 | 578.8 | 590 | 646 | 620 | 637.9 | 238 | 186.4 | 163.5 | 259.6 | 572.6 | 709.5 | 69 | 624 | 705.1 | 722.7 | 765.8 | 504.2 | 674.1 | 726.3 | 659.4 | 620 | 522.1 | 512.5 | 592 | 649 | 687 | 655 |  | 765.8 | 69
HZ | 49.985 | 50.015 | 49.971 | 50.012 | 50.029 | 50.052 | 49.876 | 49.876 | 49.985 | 50.03 | 50.016 | 50.079 | 50.053 | 50.046 | 50.034 |  | 49.991 | 50.035 | 50.031 | 49.998 | 50.063 | 50.054 | 50.0638 | 49.991 | 49.952 | 49.947 | 50.1 | 49.93 | 50.06 | 50.08 | 49.88 |  | 50.1 | 49.876
HTD 132KV | 128.9 | 129.5 | 128.9 | 129 | 128.2 | 128.2 | 129.3 | 129.3 | 127.8 | 126.3 | 125.1 | 126.2 | 127.7 | 126.8 | 125.6 |  | 124.9 | 126.6 | 124.7 | 125.8 | 131.7 | 127.5 | 127.5 | 127 | 126.7 | 127.2 | 128 | 128 | 127 | 128.8 | 127.6 |  | 131.7 | 124.7
SUI 132KV | 132.9 | 133.2 | 132.9 | 132.8 | 131 | 132.2 | 132.7 | 132.7 | 129.9 | 129 | 126.8 | 128.4 | 129.7 | 129.5 | 128.3 |  | 127.8 | 129.5 | 128.4 | 129.5 | 133.4 | 129.6 | 129.6 | 128.7 | 128.4 | 129 | 130 | 130 | 130.6 | 133 | 66.2 |  | 133.4 | 66.2
DUBI 132KV | 129.7 | 131.7 | 131.7 | 128.1 | 129.3 | 130.5 | 128 | 128 | 127.4 | 127.4 | 127.8 | 128.7 | 129.6 | 126.5 | 126.6 |  | 127.5 | 127.4 | 124.8 | 123.6 | 126.6 | 126.3 | 126.3 | 122.6 | 128 | 123.4 | 125 | 125 | 126 | 129 | 127 |  | 131.7 | 122.6
ANAMANI 132KV | 132.4 | 134.3 | 134.8 | 130.9 | 132.5 | 133.1 | 131 | 126.5 | 126.5 | 126.4 | 125.5 | 125.7 | 126.7 | 124.3 | 125.4 |  | 126.8 | 126.3 | 124.1 | 121.6 | 125 | 124.6 | 124.6 | 122.2 | 127.7 | 123.9 | 127 | 127 | 129 | 131.8 | 130 |  | 134.8 | 121.6
KG-A 132KV | 129.4 | 129.8 | 129.8 | 130.6 | 130.8 | 133.5 | 135 | 134.2 | 134.2 | 135.8 | 134.3 | 134.1 | 136.2 | 134.8 | 131.4 |  | 132.4 | 134.1 | 132.7 | 134.1 | 137.3 | 132.4 | 132.4 | 134 | 136.4 | 132.1 | 136 | 136 | 134 | 132.8 | 130.6 |  | 137.3 | 129.4
KOHALPUR 132KV | 128.8 | 133.3 | 133.5 | 135.2 | 136.4 | 130.5 | 134 | 126.2 | 126.2 | 129.4 | 129.4 | 127.4 | 131.2 | 128.8 | 130 |  | 130.1 | 130.4 | 130.9 | 131.8 | 136.5 | 132 | 132 | 131.8 | 137 | 133.5 | 131 | 131 | 128 | 130 | 128 |  | 137 | 126.2
SUI 66KV | 66.8 | 67.2 | 67.1 | 67 | 66.6 | 66.5 | 66.8 | 66 | 65.3 | 64.7 | 63.5 | 64.4 | 65.2 | 65 | 64.4 |  | 63.8 | 65.1 | 64.3 | 65.2 | 66.9 | 65.1 | 65.1 | 64.8 | 64.3 | 64.9 | 65.6 | 65.6 | 65.7 | 66.8 | 66.3 |  | 67.2 | 63.5
[33 empty] | 0 | 0
Kathmandu Load | 152.04 | 141.2 | 135.06 | 140.96 | 145.86 | 184.86 | 200.84 | 211.338 | 323.92 | 329.86 | 353.8 | 355.48 | 318.24 | 292.34 | 42 | 82.34 | 275 | 277.956 | 278.038 | 288.501 | 269.59 | 277.74 | 309.04 | 378.988 | 396.225 | 374.732 | 313.44 | 318.44 | 285.44 | 215.54 | 156.74 |  | 396.225 | 42
MRS-SYU | -6 | -6.3 | -15.7 | -19.7 | -14.7 | -7.5 | 5.3 | 19.7 | 41.5 | 42.5 | 35.9 | 40.9 | 52 | 30.6 | 22.4 |  | 30.7 | 26.7 | 27.6 | 24.4 | 33.8 | 6.6 | 11.3 | 25.7 | 36.8 | 33.2 | 28 | 25 | 17 | 11.5 | 4.6 | 75 | 52 | -19.7
NMRS-MATA | -13.4 | -13.2 | -26.4 | -32.9 | -23.8 | -12.7 | -12.1 | 28.6 | 53 | 57.3 | 48.5 | 56.2 | 70.5 | 42.6 | 23.4 |  | 36.3 | 30.3 | 34.4 | 29.2 | 47.5 | 11 | 16.9 | 34.1 | 48.5 | 45.7 | 38 | 36 | 19 | 12.4 | 2.7 | 240 | 70.5 | -32.9
KL2-MATA | -9.2 | -12 | -7.3 | -5.4 | -10.2 | -0.5 | 0 | -31.8 | 21 | 8.3 | 17.2 | 15 | 7 | 9 | 12 |  | -2 | -3.4 | 0 | 5.2 | 15 | 32.4 | 42 | 60.2 | 53 | 48 | 19 | 35 | 30 | 5 | -10 | 240 | 60.2 | -31.8
KL1-SYU | -6.4 | -8.1 | -7.7 | -5.2 | -9.6 | -6.8 | 0.2 | -3.1 | 14.1 | 17.4 | 19.8 | 20 | 18 | 14 | 5 |  | 1 | 5.3 | 0.9 | 20.5 | 24.7 | 16.9 | 16 | 22.2 | 18.3 | 18.1 | 5 | 9 | 6 | 3.2 | -4 | 60 | 24.7 | -9.6
KHIMTI-LAMOSANGHU | 94.4 | 88.16 | 99.52 | 111.52 | 111.52 | 119.72 | 114.8 | 105.298 | 101.68 | 111.52 | 137.76 | 124.64 | 72 | 98.4 | 124.64 |  | 104.96 | 108.216 | 115.898 | 114.061 | 58.45 | 122 | 135 | 144.288 | 146.125 | 146.292 | 140 | 130 | 130 | 100 | 80 | 120 | 146.292 | 58.45
LAMOSHANGU-BHAKTAPUR | 72 | 69 | 74.5 | 78.6 | 78 | 82.5 | 79.8 | 77.1 | 73.9 | 79 | 91.6 | 83.6 | 59 | 70 | 85.4 |  | 75 | 75.5 | 79.6 | 78.3 | 50.3 | 82.4 | 89.5 | 92.5 | 93 | 75 | 93 | 87 | 87 | 73 | 68
BALAJU-SYUCHATAR | 56 | 55 | 68.3 | 72.7 | 63.9 | 48.4 | 52.7 | 26.9 | -28.9 | -23.1 | -13.6 | -23 | -44 | -12 | 17 |  | 8.3 | 13.7 | 17.1 | 8.4 | -45.6 | 3.8 | 1.5 | -28.7 | -37.8 | -25.9 | -15 | -15 | 11 | 22 | 35
DHALKE-NAWALPUR I | 79.4 | 75 | 81.3 | 89.8 | 88.9 | 93.7 | 92.6 | 88 | 81.2 | 63.9 | 80.6 | 66 | 42 | 65 | 77 |  | 60 | 64.9 | 65 | 63.5 | 27 | 80 | 92.8 | 75 | 76.8 | 74.8 | 76 | 80 | 85 | 78 | 80 |  | 93.7 | 27
N. BHARATPUR-BARDGHAT I | 18.2 | 21 | 25.6 | 36.8 | 39.2 | 31.4 | 26.9 | 0 | -21.9 | -25 | -24.1 | -17 | -24 | -6 | 5 |  | -4.5 | -6.2 | -10.4 | -9 | -10.2 | 6.8 | 8.3 | -9.6 | -7.7 | -5.2 | 0 | -2.5 | 2.5 | 7.2 | -13 |  | 39.2 | -25
DAMAK-DUHABI | -13.6 | -15 | -11.6 | -9.9 | -11.9 | -20.8 | -19.8 | -25.6 | -45 | -46 | -51.5 | -50 | -42 | -34 | -29 |  | -24 | -26.7 | -29.9 | -38.6 | -38 | -42.4 | -50.4 | -60.3 | -52.5 | -47.6 | -41 | -41 | -28 | -20.5 | -15 |  | -9.9 | -60.3
HETAUDA-KAMANE | -23.1 | -22 | -34.2 | -33.8 | -32.5 | -31 | -29.3 | 16.1 | -7.1 | 9.3 | -4.5 | -3.5 | 16.8 | -1.7 | 17 |  | 30 | 29.8 | 30.9 | 29.1 | 9.6 | -37.3 | -44 | -43.2 | -38.2 | -37.2 | -38 | -36 | -38 | -14 | -12 |  | 30.9 | -44
MIRCHAIYA LAHAN 2 | 100.2 | 95.1 | 92.3 | 91.5 | 91.3 | 84.7 | 91.1 | 96.4 | 107.3 | 105 | 103.1 | 100.8 | 93.3 | 119 | 112 |  | 114 | 122.6 | 116 | 116.4 | 112.5 | 115 | 103 | 123.5 | 119.8 | 120.7 | 128 | 128 | 117 | 107 | 104 |  | 128 | 84.7
Water Level
UTK | 1984.22 | 1984.42 | 1984.67 | 1984.9 | 1985.1 | 1985.35 |  | 1985.52 |  | 1985.42 |  | 1984.4 | 1983.55 | 1983.45 | 1983.6 | 1983.8 | 1984 | 1984.22 | 1984.45 | 1984.62 | 1984.825 |  | 1985.02 |  | 1984.87 |  | 1984.2 |  | 1983.6 | 1983.5
KGA | 520.78 | 521.12 | 521.45 | 521.73 | 522.03 | 522.31 |  | 522.43 |  | 522.03 |  | 521.57 | 521.08 | 520.78 | 520.84 | 521.02 | 521.1 | 520.99 | 520.76 | 520.56 | 520.6 |  | 520.8 |  | 520.68 |  | 520.42 |  | 520.28 | 520.25 | 520.35
MMRS | 622.37 | 622.24 | 622.44 | 623 | 623.3 | 623.12 |  | 623.09 |  | 622.99 |  | 622.85 | 622.8 | 622.66 | 622.56 | 622.6 | 622.67 | 622.7 | 622.45 | 622.35 | 622.31 |  | 622.3 |  | 622.15 |  | 622.05 | 622.06 | 622.03 | 622.16 | 622.29
MRS | 335.62 | 335.9 | 336.19 | 336.5 | 336.7 | 336.8 |  | 336.8 |  | 336.54 |  | 336.24 | 335.92 | 335.46 | 335.12 | 334.85 | 334.89 | 334.87 | 334.97 | 335.12 | 335.27 |  | 335.47 |  | 335.41 |  | 335.1 | 335.05 | 335.03 | 335.39 | 335.39
CHM | 883.8 | 884.5 | 885.2 | 885.8 | 886.2 | 886.8 |  | 887.1 |  | 886.8 |  | 885.8 | 885.6 | 885.6 | 885.6 | 885.5 | 885.1 | 885 | 884.7 | 884.6 | 884.4 |  | 885.1 |  | 885.2 |  |  | 884.4 |  | 884.3
KL 1 | 0: 1519.79; 0.29167: 1519.8; 0.70833: 1519.78
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1705.39; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/23)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 24
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/24 |  |  | 2080/10/24 |  |  | Thursday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 572.9 | 601.3 | 593.6 | 582.8 | 599.7 | 662.7 | 670.5 | 650.3 | 291.7 | 145.7 | 138.1 | 436.6 | 611.3 | 677.3 | 720.8 | 717.1 | 783.2 | 732.7 | 813.8 | 695.7 | 563.9 | 563.6 | 500.6 | 441.5 | 349.6 | 332.5 | 475.2 | 597.9 | 664.3 | 712.2 | 602.9
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1643MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1206 | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1354.69 | 1449.59 | 1522.39 | 1464.14 | 1642.99 | 1571.79 | 1473.99 | 1529.69 | 1536.79 | 1399.09 | 1445.39 | 1473.79 | 1419.69 | 1495.79 | 1370.79 | 1361.99 | 1400.67 | 1654.19 | 1763.79 | 1689.59 | 1627.59 | 1583.59 | 1535.49 | 1368.69 | 1306.89
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1571.79 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1571.79 MW
Solu Khola Dudhkoshi(86) | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 86 | 23.3 | 22.9
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 24
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 54 | 10 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/24)
Likhu-IV(52.4) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 52.4 | 14 | 14
Upper Marsyangdi "A"(50) | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 50 | 25.5 | 25.5 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 45 | 15.4 | 15.4 |  | IPP | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 38.1 | 38.1 | 38.1 | 38.1 | 38.1 | 38.1 | 108.1 | 408.1 | 437 | 107 | 52 | 38
Mistri Khola(42) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42 | 6 | 6 |  | NEA ROR PROR | 142.04 | 142.04 | 142.04 | 126.54 | 126.54 | 157.54 | 212.04 | 305.39 | 337.74 | 271.44 | 207.44 | 212.54
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 602.9 | 572.9 | 601.3 | 593.6 | 582.8 | 599.7 | 670.5 | 291.7 | 138.1 | 436.6 | 611.3 | 677.3
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 150
Nyadi(30) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 30 | 7.2 | 7.2 |  | System_Load | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1449.59 | 1464.14 | 1571.79 | 1473.99 | 1529.69 | 1536.79
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 28 | 6.7 | 6.7 |  | National_Load | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1449.59 | 1464.14 | 1571.79 | 1473.99 | 1529.69 | 1536.79
Dordi(27) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 30 | 5.4 | 5.4
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 8.3 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 25 | 6.8 | 6.8
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 9.3 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 12 | 4 | 4
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 0.83333: 15.4; 0.85417: 15.4; 0.875: 15.4; 0.91667: 15.4; 0.95833: 15.4 | 240 | 15.4 | 15.4
Total IPP | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 459.35 | 459.35 | 459.35 | 459.35 | 459.35 | 1042.4 | 459.35 | 458.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 130 | 370 | 456 | 400 | 70 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 300 | 350 | 350 | 200 | 70 | 15 | 0 | 456 | 456 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 10.1 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 8.2 | 8.2 | 22.1 | 11.1 | 8.2
Total NEA SUBSIDIARIES | 38.1 | 38.1 | 38.1 | 38.1 | 38.1 | 38.1 | 38.1 | 108.1 | 168.1 | 408.1 | 493.1 | 437 | 107 | 52 | 38 | 38 | 88 | 38 | 38 | 38 | 38 | 36 | 36 | 236 | 338.1 | 388.1 | 388.1 | 238.1 | 108.1 | 50.2 | 35.2 | 538.1 | 493.1 | 35.2
KGA(144) | 30 | 30 | 30 | 30 | 30 | 49 | 49 | 81.5 | 81.2 | 120.25 | 140.5 | 133 | 81 | 61 | 60.6 | 30 | 30 | 30 | 30 | 30 | 30 | 49.4 | 83.8 | 134.5 | 130 | 100.9 | 60 | 60 | 48.8 | 30.5 | 0 | 144 | 140.5 | 0
Middle MRS(70) | 24 | 24 | 24 | 22.8 | 22.8 | 34.8 | 34.8 | 25 | 24.9 | 34.8 | 34.8 | 34.8 | 35 | 29 | 24.3 | 24.3 | 24.3 | 35 | 35 | 35 | 35 | 23.7 | 23.7 | 23.7 | 27.3 | 22.5 | 22.3 | 22.3 | 22.4 | 22.5 | 0 | 70 | 35 | 0
MRS(69) | 16.6 | 16.6 | 16.6 | 0 | 0 | 0 | 22.4 | 16.8 | 34.2 | 45.6 | 66.8 | 66.8 | 66 | 33 | 34 | 33.4 | 33.4 | 22.1 | 22.1 | 22.1 | 22.1 | 44.3 | 45.9 | 68 | 68.6 | 68.4 | 68.4 | 68.4 | 67.9 | 45.3 | 16.5 | 69 | 68.6 | 0
U Trisuli 3A(60) | 32 | 32 | 32 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 36.5 | 36.5 | 36.5 | 36.5 | 35 | 35 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 33.3 | 33.3 | 33.5 | 35.3 | 35.5 | 60 | 36.5 | 32
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 28.8 | 28.8 | 23.5 | 23.5 | 10 | 0 | 0 | 0 | 0 | 14.7 | 14.7 | 14.7 | 14.7 | 10.4 | 13.98 | 23 | 28.2 | 28 | 27.7 | 23.1 | 14.5 | 9.8 | 9.9 | 30 | 28.8 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 3.7 | 5 | 10 | 18.9 | 18.9 | 18.9 | 17.1 | 13.5 | 8.5 | 1.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.9 | 0 | [14 empty] | Tanakpur | 55 | 62 | 54.6 | 55.7 | 44.6 | 48.9 | 57.1 | 62.3 | 56.6 | 66 | 65 | 54.6 | 52.4 | 65.5 | 60.8 | 66 | 45.2 | 67.6 | 70.6 | 66.8 | 65.4 | 59.9 | 67 | 54
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 15 | 2 | 2 | [14 empty] | Muz | 412 | 416 | 414.6 | 408.4 | 438.2 | 405.8 | 56.6 | 8 | 274 | 436 | 425 | 450 | 473 | 486.4 | 510.4 | 542.2 | 514.3 | 449.9 | 284.8 | 189 | 404.6 | 376.5 | 411.1 | 425
DEVI(14.1) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 14.1 | 9.3 | 8.1 | [14 empty] | Ram | 4 | 3.3 | 3.8 | 3.3 | 3.7 | 32.9 | 33.4 | 4.2 | 30 | 33.7 | 34.5 | 45.7 | 27 | 40.7 | 10.3 | 45.6 | 26.7 | 3 | 4.7 | 4 | 54.7 | 49.3 | 55.2 | 3.9
MODI(14) | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 14 | 3.4 | 3.4 | [14 empty] | Rax | 102 | 120 | 120.6 | 115.4 | 113.2 | 126.8 | 74.2 | 0 | 0 | 0 | 90 | 106 | 100 | 126.8 | 97.8 | 101.2 | 53.8 | 0 | 0 | 0 | 0 | 108.8 | 110.8 | 120
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 0 | 0 | 0 | 0 | 0 | 56.1 | 70.4 | 63.6 | 76 | 75.6 | 62.8 | 64.5 | 64.7 | 63.8 | 53.4 | 58.8 | 55.7 | 43.1 | 81.4 | 72.7 | 73.2 | 69.8 | 68.1 | 0
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 55 | 62 | 54.6 | 55.7 | 44.6 | 48.9 | 57.1 | 62.3 | 56.6 | 66 | 65 | 54.6 | 52.4 | 65.5 | 60.8 | 66 | 45.2 | 67.6 | 70.6 | 66.8 | 65.4 | 59.9 | 67 | 54
Total ROR | 142.04 | 142.04 | 142.04 | 126.54 | 126.54 | 157.54 | 194.94 | 212.04 | 245.04 | 305.39 | 345.24 | 337.74 | 271.44 | 207.44 | 212.54 | 181.34 | 181.34 | 193.64 | 190.04 | 185.04 | 178.14 | 203.14 | 242.12 | 323.94 | 328.84 | 294.54 | 249.94 | 245.34 | 225.34 | 181.64 | 100.14 | 489.91 | 345.24 | 100.14 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.77083: 20; 0.79167: 60; 0.8125: 60; 0.83333: 60; 0.85417: 55; 0.875: 60; 0.91667: 0; 0.95833: 0 | 60 | 60 | 0 | [15 empty] | 412 | 416 | 414.6 | 408.4 | 438.2 | 405.8 | 56.6 | 8 | 274 | 436 | 425 | 450 | 473 | 486.4 | 510.4 | 542.2 | 514.3 | 449.9 | 284.8 | 189 | 404.6 | 376.5 | 411.1 | 425
KL2(32) | 0.77083: 10.6; 0.79167: 25.8; 0.8125: 28.1; 0.83333: 27.6; 0.85417: 22.4; 0.875: 25.5; 0.91667: 9.7; 0.95833: 0 | 32 | 28.1 | 0 | [15 empty] | 4 | 3.3 | 3.8 | 3.3 | 3.7 | 32.9 | 33.4 | 4.2 | 30 | 33.7 | 34.5 | 45.7 | 27 | 40.7 | 10.3 | 45.6 | 26.7 | 3 | 4.7 | 4 | 54.7 | 49.3 | 55.2 | 3.9
KL3(14) | 0.77083: 4.1; 0.79167: 10.6; 0.8125: 10.3; 0.83333: 10.1; 0.85417: 8.2; 0.875: 9.3; 0.91667: 3.5; 0.95833: 0 | 14 | 10.6 | 0 | [15 empty] | 102 | 120 | 120.6 | 115.4 | 113.2 | 126.8 | 74.2 | 0 | 0 | 0 | 90 | 106 | 100 | 126.8 | 97.8 | 101.2 | 53.8 | 0 | 0 | 0 | 0 | 108.8 | 110.8 | 120
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7 | 96.4 | 98.4 | 97.7 | 85.6 | 94.8 | 13.2 | 0 | 106 | 98.4 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 56.1 | 70.4 | 63.6 | 76 | 75.6 | 62.8 | 64.5 | 64.7 | 63.8 | 53.4 | 58.8 | 55.7 | 43.1 | 81.4 | 72.7 | 73.2 | 69.8 | 68.1 | 0
TANAKPUR | 54 | 55 | 62 | 54.6 | 55.7 | 44.6 | 50.5 | 48.9 | 51.6 | 57.1 | 60.2 | 62.3 | 56.6 | 66 | 65 | 54.6 | 52.4 | 65.5 | 60.8 | 66 | 45.2 | 61.9 | 67.6 | 62.9 | 70.6 | 58.1 | 66.8 | 60.9 | 65.4 | 59.9 | 67 |  | 70.6 | 44.6
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 425 | 412 | 416 | 414.6 | 408.4 | 438.2 | 443.7 | 405.8 | 379.4 | 56.6 | 8.9 | 8 | 274 | 436 | 425 | 450 | 473 | 486.4 | 510.4 | 542.2 | 514.3 | 443.8 | 449.9 | 348 | 284.8 | 199.2 | 189 | 339 | 404.6 | 376.5 | 411.1 |  | 542.2 | 8
RAMNAGAR | 3.9 | 3.9 | 3.3 | 3.8 | 3.3 | 3.7 | 4.3 | 32.9 | 41.8 | 33.4 | 6.2 | 4.2 | 30 | 33.7 | 34.5 | 45.7 | 27 | 40.7 | 10.3 | 45.6 | 26.7 | 3.2 | 3 | 5 | 4.7 | 4.1 | 4 | 3.7 | 54.7 | 49.3 | 55.2 |  | 55.2 | 3 | [22 empty] | 55 | 0 | 412 | 4 | 102 | 0
RAXAUL 132 | 120 | 102 | 120 | 120.6 | 115.4 | 113.2 | 112.2 | 126.8 | 98.2 | 74.2 | 0 | 0 | 0 | 0 | 90 | 106 | 100 | 126.8 | 97.8 | 101.2 | 53.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8 | 110.8 |  | 126.8 | 0 | [22 empty] | 62 | 0 | 416 | 3.3 | 120 | 0
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 54.6 | 0 | 414.6 | 3.8 | 120.6 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 55.7 | 0 | 408.4 | 3.3 | 115.4 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 44.6 | 0 | 438.2 | 3.7 | 113.2 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 48.9 | 0 | 405.8 | 32.9 | 126.8 | 56.1
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 57.1 | 0 | 56.6 | 33.4 | 74.2 | 70.4
SAMPATIYA 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 56.1 | 79.3 | 70.4 | 70.4 | 63.6 | 76 | 75.6 | 62.8 | 64.5 | 64.7 | 63.8 | 53.4 | 58.8 | 55.7 | 55 | 43.1 | 84.7 | 81.4 | 88.2 | 72.7 | 71.6 | 73.2 | 69.8 | 68.1 |  | 88.2 | 0 | [22 empty] | 62.3 | 0 | 8 | 4.2 | 0 | 63.6
Total IMPORT | 602.9 | 572.9 | 601.3 | 593.6 | 582.8 | 599.7 | 662.7 | 670.5 | 650.3 | 291.7 | 145.7 | 138.1 | 436.6 | 611.3 | 677.3 | 720.8 | 717.1 | 783.2 | 732.7 | 813.8 | 695.7 | 563.9 | 563.6 | 500.6 | 441.5 | 349.6 | 332.5 | 475.2 | 597.9 | 664.3 | 712.2 | 0 | 813.8 | 138.1 | [22 empty] | 56.6 | 0 | 274 | 30 | 0 | 76
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 66 | 0 | 436 | 33.7 | 0 | 75.6
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 65 | 0 | 425 | 34.5 | 90 | 62.8
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 54.6 | 0 | 450 | 45.7 | 106 | 64.5
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 52.4 | 0 | 473 | 27 | 100 | 64.7
TOTAL SYSTEM LOAD (ACTUAL) | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1354.69 | 1449.59 | 1522.39 | 1464.14 | 1442.99 | 1371.79 | 1273.99 | 1329.69 | 1386.79 | 1399.09 | 1445.39 | 1473.79 | 1419.69 | 1495.79 | 1370.79 | 1261.99 | 1300.67 | 1554.19 | 1663.79 | 1589.59 | 1527.59 | 1503.59 | 1485.49 | 1368.69 | 1306.89 | 2231.81 | 1663.79 | 1206.39 | [22 empty] | 65.5 | 0 | 486.4 | 40.7 | 126.8 | 63.8
Interruption/Tripping | 0: 0; 0.041667: 0; 0.3125: 200; 0.33333: 200; 0.375: 200; 0.41667: 200; 0.45833: 150; 0.72917: 100; 0.75: 100; 0.77083: 100; 0.79167: 100; 0.8125: 100; 0.83333: 100; 0.85417: 80; 0.875: 50 |  | 200 | 0 | [22 empty] | 60.8 | 0 | 510.4 | 10.3 | 97.8 | 53.4
TOTAL SYSTEM LOAD (EXPECTED) | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1354.69 | 1449.59 | 1522.39 | 1464.14 | 1642.99 | 1571.79 | 1473.99 | 1529.69 | 1536.79 | 1399.09 | 1445.39 | 1473.79 | 1419.69 | 1495.79 | 1370.79 | 1361.99 | 1400.67 | 1654.19 | 1763.79 | 1689.59 | 1627.59 | 1583.59 | 1535.49 | 1368.69 | 1306.89 | 1693.71 | 1763.79 | 1206.39 | [22 empty] | 66 | 0 | 542.2 | 45.6 | 101.2 | 58.8
TOTAL NATIONAL LOAD (ACTUAL) | 1241.99 | 1211.99 | 1240.39 | 1217.19 | 1206.39 | 1254.29 | 1354.69 | 1449.59 | 1522.39 | 1464.14 | 1642.99 | 1571.79 | 1473.99 | 1529.69 | 1536.79 | 1399.09 | 1445.39 | 1473.79 | 1419.69 | 1495.79 | 1370.79 | 1361.99 | 1400.67 | 1654.19 | 1763.79 | 1689.59 | 1627.59 | 1583.59 | 1535.49 | 1368.69 | 1306.89 |  | 1763.79 | 1206.39 | [22 empty] | 45.2 | 0 | 514.3 | 26.7 | 53.8 | 55.7
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67.6 | 0 | 449.9 | 3 | 0 | 43.1
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 70.6 | 0 | 284.8 | 4.7 | 0 | 81.4
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 66.8 | 0 | 189 | 4 | 0 | 72.7
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 65.4 | 0 | 404.6 | 54.7 | 0 | 73.2
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 59.9 | 0 | 376.5 | 49.3 | 108.8 | 69.8
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 67 | 0 | 411.1 | 55.2 | 110.8 | 68.1
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 54 | 0 | 425 | 3.9 | 120 | 0
NET IMPORT | 602.9 | 572.9 | 601.3 | 593.6 | 582.8 | 599.7 | 662.7 | 670.5 | 650.3 | 291.7 | 145.7 | 138.1 | 436.6 | 611.3 | 677.3 | 720.8 | 717.1 | 783.2 | 732.7 | 813.8 | 695.7 | 563.9 | 563.6 | 500.6 | 441.5 | 349.6 | 332.5 | 475.2 | 597.9 | 664.3 | 712.2 |  | 813.8 | 138.1
HZ | 49.94 | 50.01 | 50.02 | 50.043 | 50 | 50.02 | 50.02 | 50.01 | 50.07 | 49.85 | 49.87 | 50.114 | 49.982 | 49.951 | 50 | 50.123 | 50.046 | 50 | 49.93 | 49.93 | 49.96 | 50.11 | 50.07 | 50.01 | 49.95 | 49.92 | 49.987 | 49.923 | 50.074 | 49.99 | 50.044 |  | 50.123 | 49.85
HTD 132KV | 127 | 129 | 129 | 129 | 130.2 | 130.2 | 130.2 | 128.5 | 126.4 | 127.6 | 125.3 | 125.3 | 127.1 | 124.7 | 126 | 122.8 | 123.4 | 124.1 | 124.1 | 123.2 | 126.4 | 129.1 | 127.7 | 126.1 | 124.7 | 126.6 | 126.8 | 126.3 | 128 | 130.4 | 129.2 |  | 130.4 | 122.8
SUI 132KV | 132 | 132 | 132 | 132 | 133.5 | 133.5 | 133.5 | 131.5 | 129.4 | 129.1 | 127.3 | 127.8 | 129.6 | 127.5 | 128.7 | 126.4 | 126.8 | 129.1 | 129.1 | 126.9 | 129.2 | 131.4 | 130.2 | 129.3 | 128.1 | 128.1 | 130.3 | 130.4 | 131.9 | 133.8 | 133.3 |  | 133.8 | 126.4
DUBI 132KV | 131 | 131 | 131 | 131 | 132.1 | 132.1 | 132.1 | 128.1 | 127.3 | 126.3 | 125.9 | 127 | 128.2 | 123.1 | 124 | 126.9 | 123.2 | 123.4 | 123.4 | 123.9 | 127.5 | 130.5 | 128.8 | 128.8 | 126.6 | 126.6 | 131.7 | 124.9 | 125.4 | 129.7 | 130.1 |  | 132.1 | 123.1
ANAMANI 132KV | 133 | 133 | 133 | 133 | 134 | 134 | 134 | 130.2 | 127.5 | 125.6 | 123.8 | 123.4 | 127.2 | 123.1 | 123.3 | 127.1 | 123.8 | 123.2 | 123.2 | 123.2 | 126.3 | 128.8 | 125.8 | 125.8 | 125.3 | 125.3 | 132.1 | 126.6 | 127.5 | 131.7 | 132.2 |  | 134 | 123.1
KG-A 132KV | 129 | 133 | 132 | 132 | 133.4 | 133.4 | 133.4 | 134.4 | 132.5 | 135.9 | 133.3 | 131.8 | 133.7 | 132.5 | 132.2 | 129.7 | 128.8 | 133.6 | 133.6 | 131.5 | 134.8 | 134.8 | 133.1 | 133.1 | 132.8 | 132.8 | 135 | 134.9 | 135.4 | 134.8 | 134.1 |  | 135.9 | 128.8
KOHALPUR 132KV | 132 | 119 | 134 | 134 | 131 | 131 | 131 | 130.9 | 122.9 | 135 | 127.2 | 131.8 | 133 | 129.4 | 131.5 | 134.8 | 133 | 134 | 134 | 128.8 | 133.6 | 133.6 | 130.7 | 130.7 | 132.1 | 132.1 | 131.7 | 135.3 | 133.3 | 135.4 | 129 |  | 135.4 | 119
SUI 66KV | 66 | 66 | 66.6 | 66.6 | 67.2 | 67.2 | 67.2 | 65.8 | 64.9 | 64.8 | 64.2 | 64.5 | 65.3 | 64.1 | 64.7 | 63.5 | 63.9 | 64.5 | 64.5 | 64 | 65.4 | 65.4 | 65.4 | 65.4 | 64.5 | 64.5 | 65.3 | 65.4 | 66.2 | 67.2 | 67.2 |  | 67.2 | 63.5
[33 empty] | 0 | 0
Kathmandu Load | 133.44 | 138.44 | 140.44 | 132.1 | 135.7 | 157.56 | 190.9 | 225.56 | 280.88 | 320.9 | 352.96 | 343.34 | 306.54 | 293.02 | 42 | 285.04 | 262.24 | 279.32 | 276.32 | 273.44 | 283.58 | 280.32 | 299.48 | 363.6 | 381.7 | 362.84 | 296.601 | 279.046 | 249.657 | 225.012 | 178.176 |  | 381.7 | 42
MRS-SYU | -9 | -5 | -10 | -15.4 | -16.9 | -12.6 | 3.4 | 12.7 | 17.8 | 34.4 | 39.6 | 40.7 | 48.3 | 33.6 | 28.3 | 14.3 | 14 | 17.8 | 16.4 | 10.9 | 19.8 | 16.3 | 18.36 | 34.1 | 23.6 | 21.1 | 18.7 | 19.6 | 27.8 | 20 | 1 | 75 | 48.3 | -16.9
NMRS-MATA | -15 | -10 | -17 | -22.9 | -25.2 | -18.9 | 1.9 | 13.6 | 18.7 | 46.9 | 55.2 | 57.6 | 67.2 | 48.3 | 40.5 | 14.4 |  | 18.8 | 17.8 | 10.6 | 19.4 | 23.6 | 26.6 | 45.7 | 31.2 | 28.7 | 25.4 | 26.3 | 30.7 | 22 | -3.2 | 240 | 67.2 | -25.2
KL2-MATA | -10 | -14 | -10 | -11.5 | -9 | -5 | -3 | 4 | 20.4 | 21.3 | 18 | 8 | 2 | 3 | 17.6 | 9 |  | 9 | 9 | 11 | 19 | 15 | 21.8 | 28 | 33 | 27 | -16 | -20 | -30.5 | 8.6 | -2.9 | 240 | 33 | -30.5
KL1-SYU | -6 | -6 | -6 | -5.6 | -5.5 | -4 | -2.9 | -1.2 | 3.4 | 13.4 | 17.8 | 22.4 | 15.6 | 10 | 9.5 | 2.5 | 3.2 | 1.4 | -2.8 | -1.5 | 4.4 | 23.2 | 23.1 | 32.1 | 48.6 | 46.5 | 37.5 | 33 | 29.2 | 2.7 | -4 | 60 | 48.6 | -6
KHIMTI-LAMOSANGHU | 90 | 90 | 100 | 101.76 | 106.56 | 112.32 | 105.76 | 110.72 | 132.64 | 116.96 | 130.72 | 123 | 82 | 101.68 | 100 | 139.2 | 139.4 | 128.48 | 135.68 | 147.2 | 132.64 | 114.88 | 122.88 | 136.96 | 158.56 | 152.8 | 147.461 | 136.606 | 108.717 | 86.172 | 101.536 | 120 | 158.56 | 82
LAMOSHANGU-BHAKTAPUR | 79 | 79 | 75 | 72.8 | 75.6 | 77.9 | 75.2 | 77.2 | 88.7 | 80.7 | 87.9 | 82 | 60 | 71 | 70.1 | 92.5 | 91 | 85.5 | 89.3 | 96.6 | 87.9 | 77.7 | 82.5 | 89.4 | 98.9 | 98.2 | 93.8 | 88.3 | 75.2 | 64.3 | 72.4 |  | 98.9 | 60
BALAJU-SYUCHATAR | 57 | 57 | 54 | 62 | 59.7 | 55 | 39.1 | 24.1 | 14.8 | -20.8 | -24.9 | -25 | -41 | -14 | -12.7 | 34 | 35 | 24.5 | 28 | 39.1 | 18.3 | 2.4 | -5.1 | -23.4 | -7.8 | -3.4 | 5.1 | 3.9 | 1.7 | 0.8 | 36.6 |  | 62 | -41
DHALKE-NAWALPUR I | 89 | 89 | 87 | 80.6 | 83.4 | 87.5 | 82 | 79.5 | 87.6 | 64.1 | 67.8 | 68 | 57 | 76.5 | 68.5 | 86 | 86 | 77.6 | 81.2 | 92 | 83.3 | 82.7 | 82.8 | 89.7 | 108.8 | 97.5 | 98.7 | 100.1 | 89.6 | 64.1 | 77.6 |  | 108.8 | 57
N. BHARATPUR-BARDGHAT I | 35 | 35 | 41 | 38.3 | 38.5 | 34.6 | 22 | 0 | -4.9 | -13.6 | -16 | -18 | -20 | -16 | -7.1 | 5.1 |  | -1.9 | 0 | 3.3 | 8.7 | 7.9 | 4.9 | -7.5 | 5.6 | 6.8 | 11.3 | 8.7 | 0 | 0 | 8.5 |  | 41 | -20
DAMAK-DUHABI | -14 | -14 | -12 | -10 | -12.5 | -15.5 | -22.3 | -29.5 | -40.3 | -45.4 | -49.5 | -53 | -37 | -30 | -35.8 | -27 | -24 | -28.3 | -30.9 | -37.5 | -44.2 | -48.9 | -54.3 | -55.3 | -53.6 | -47.7 | -39.7 | -35.2 | -30 | -21.2 | -15.2 |  | -10 | -55.3
HETAUDA-KAMANE | -24 | -24 | -25 | -27.3 | -24 | -26.1 | -20.4 | -16.4 | -22.4 | -10.5 | 0 | 11.5 | 19 | 5.5 | -11.8 | 31 | 31.3 | 31.4 | 27.9 | 29.5 | 19.3 | 11.4 | 11.1 | 0 | 6.5 | 4.5 | 5.2 | 5.5 | 7.4 | -7.6 | -18.2 |  | 31.4 | -27.3
MIRCHAIYA LAHAN 2 | 94 | 94 | 94 | 83.9 | 87.3 | 92.5 | 100.2 | 104 | 108.4 | 103.4 | 110.7 | 108 | 98 | 115 | 128.5 | 117 | 111 | 122.8 | 123.4 | 117.4 | 109.7 | 109.5 | 103.6 | 118.6 | 112.8 | 106.1 | 105.7 | 118.3 | 122 | 107 | 95.6 |  | 128.5 | 83.9
Water Level
UTK | 1983.94 | 1984.14 | 1984.35 | 1984.58 | 1984.8 | 1984.99 |  | 1985.15 |  | 1985 |  | 1983.89 | 1982.64 | 1982.61 | 1982.89 | 1983.16 | 1983.29 | 1983.45 | 1983.75 | 1983.9 | 1984.1 |  | 1884.31 |  | 1984.1 |  | 1983.2 |  | 1982.5 | 1982.81 | 1983.05
KGA | 520.49 | 520.63 | 520.76 | 520.9 | 521.04 | 521.18 |  | 521.1 |  | 520.82 |  | 519.72 | 519.72 | 519.5 | 519.42 | 519.32 | 519.48 | 519.62 | 519.78 | 519.9 | 520.16 |  | 520.08 |  | 519.5 |  | 519.04 |  | 518.94 | 519.09 | 519.47
MMRS | 622.39 | 622.39 | 622.4 | 622.46 | 622.49 | 622.46 |  | 622.36 |  | 622.37 |  | 622.14 | 622.1 | 622.09 | 622.07 | 622.09 | 622.16 | 622.1 | 621.86 | 621.57 | 621.5 |  | 621.46 |  | 621.43 |  | 621.6 |  | 621.7 | 621.84 | 622.35
MRS | 335.57 | 335.77 | 335.92 | 336.09 | 336.37 | 336.61 |  | 336.75 |  | 336.76 |  | 336.23 | 336.23 | 335.92 | 335.84 | 335.78 | 335.75 | 335.53 | 335.96 | 336 | 336.07 |  | 335.96 |  | 335.71 |  | 335.28 |  | 334.84 | 334.45 | 334.5
CHM | 885.4 | 886 | 886.6 | 887 | 887.5 | 887.8 |  | 887.6 |  | 887 |  | 885.1 | 885.1 | 885.3 | 885.9 | 886.4 | 886.9 | 887 | 886.8 | 886.7 | 886.7 |  | 886.6 |  | 886 |  | 884.7 |  | 883.3 | 882.8 | 882.7
KL 1 | 0: 1519.8; 0.83333: 1519.77
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4) | 0.25: nea; 0.27083: 5055; 0.29167: 210.625
Rudi Khola A(8.8) | 0.25: sub; 0.27083: 2667; 0.29167: 111.125
Naugadh gad Khola(8.5) | 0.25: utk; 0.27083: 1852; 0.29167: 77.1667
Butwal Solar Project(8.5) | 0.25: ipp; 0.27083: 10244; 0.29167: 426.8333
Upper Hewa Khola Small(8.5) | 0.25: imp; 0.27083: 13569; 0.29167: 565.375
Ankhu Khola - 1(8.4) | 0.25: int; 0.27083: 1500; 0.29167: 62.5
Mai sana Cascade(8) | 0.27083: 34887; 0.29167: 1453.625
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69774 | 2907.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1642.99; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/24)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 25
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/25 |  |  | 2080/10/25 |  |  | Friday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 646.7 | 664.8 | 654.4 | 622.9 | 650.4 | 682.3 | 620 | 652 | 273 | 133.3 | 155 | 297.4 | 536.8 | 590.8 | 674.8 | 647 | 727.2 | 715.7 | 749.6 | 717.2 | 606.2 | 593.6 | 528.6 | 362.1 | 236.09 | 328.6 | 510.6 | 587.2 | 639.6 | 613.3 | 684
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1684MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1164 | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1351.39 | 1458.19 | 1528.99 | 1587.29 | 1652.69 | 1684.39 | 1561.39 | 1564.79 | 1342.49 | 1353.39 | 1290.19 | 1310.99 | 1288.59 | 1330.59 | 1411.69 | 1408.19 | 1478.69 | 1638.49 | 1650.49 | 1609.28 | 1500.59 | 1369.29 | 1354.99 | 1395.29 | 1164.19
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1684.39 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1684.39 MW
Solu Khola Dudhkoshi(86) | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 24.3 | 24.3 | 23 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 86 | 24.3 | 20.6
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 25
Super Dordi (54) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1 | 13.1 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 54 | 13.1 | 0 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/25)
Likhu-IV(52.4) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 52.4 | 14 | 14
Upper Marsyangdi "A"(50) | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 29.7 | 0 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 45 | 15.4 | 15.4 |  | IPP | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 461.55 | 431.85 | 404.35
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 50.2 | 141 | 416 | 481 | 101 | 36 | 86
Mistri Khola(42) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42 | 6 | 6 |  | NEA ROR PROR | 75.54 | 75.54 | 75.54 | 75.54 | 100.54 | 98.44 | 233.64 | 284.74 | 324.84 | 369.34 | 300.14 | 261.34
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 684 | 646.7 | 664.8 | 654.4 | 622.9 | 650.4 | 620 | 273 | 155 | 297.4 | 536.8 | 590.8
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 260 | 260 | 260 | 0
Nyadi(30) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 30 | 7.2 | 7.2 |  | System_Load | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1458.19 | 1587.29 | 1684.39 | 1561.39 | 1564.79 | 1342.49
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 28 | 6.7 | 6.7 |  | National_Load | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1458.19 | 1587.29 | 1684.39 | 1561.39 | 1564.79 | 1342.49
Dordi(27) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7 | 13.7 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 30 | 14.5 | 0
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 8.3 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2 | 13.2 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 25 | 13.2 | 0
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 3 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 9.3 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 9.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 9.5 | 0
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 15.4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 13.5 | 17.5 | 19.4 | 15.8 | 17.4 | 17.4 | 17.4 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 240 | 19.4 | 13.5
Total IPP | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 463.55 | 461.55 | 431.85 | 404.35 | 401.95 | 401.95 | 401.95 | 401.95 | 401.95 | 401.95 | 401.95 | 451.45 | 451.45 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 1042.4 | 463.55 | 401.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 105 | 136 | 380 | 445 | 445 | 65 | 0 | 50 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 270 | 335 | 275 | 120 | 70 | 70 | 0 | 456 | 445 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 11.2 | 11.2 | 11.2 | 11 | 8.5 | 8.5 | 8.5 | 22.1 | 11.2 | 8.2
Total NEA SUBSIDIARIES | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 50.2 | 50.2 | 141 | 172 | 416 | 481 | 481 | 101 | 36 | 86 | 86 | 51 | 36 | 36 | 36.1 | 36.1 | 36.1 | 36.1 | 186.1 | 308.2 | 373.2 | 313.2 | 158 | 105.5 | 105.5 | 35.5 | 538.1 | 481 | 35.2
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 70.2 | 70.6 | 88.7 | 96.9 | 96.9 | 141.5 | 90.3 | 71 | 81 | 81.3 | 45.3 | 30.5 | 30.4 | 30.4 | 30.1 | 60.2 | 91.4 | 122.7 | 122.3 | 81 | 86 | 49 | 35.8 | 0 | 144 | 141.5 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 25 | 24.7 | 34.7 | 34.6 | 34.6 | 60 | 70.6 | 70.6 | 59.9 | 62 | 64 | 0 | 0 | 0 | 24.5 | 35.4 | 23.7 | 24.8 | 25.4 | 45.1 | 46.1 | 66.3 | 65 | 23 | 23 | 22.1 | 0 | 70 | 70.6 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 16.9 | 44.6 | 46.7 | 45.4 | 62.9 | 62.9 | 65.4 | 42.6 | 18 | 22.2 | 22.3 | 16.5 | 0 | 0 | 17.7 | 17.8 | 21.8 | 53.8 | 69 | 69 | 68.8 | 68 | 60 | 62.6 | 0 | 69 | 69 | 0
U Trisuli 3A(60) | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 33.5 | 33.5 | 34 | 34.3 | 34.5 | 36.3 | 36.3 | 35.3 | 34.3 | 34.3 | 32.5 | 32.5 | 32.5 | 32.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.3 | 33.3 | 33.3 | 33.3 | 33 | 60 | 36.3 | 32.5
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 14.9 | 23.8 | 23.4 | 15.3 | 28.3 | 28.3 | 28.3 | 23 | 14.6 | 14 | 0 | 30 | 28.3 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 2.9 | 2.9 | 12 | 15.7 | 18.8 | 19.9 | 19.1 | 16.5 | 12.4 | 8.6 | 1.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19.9 | 0 | [14 empty] | Tanakpur | 58 | 55 | 54 | 52 | 55.4 | 64 | 53 | 60 | 63.3 | 62.8 | 51.8 | 45.8 | 48 | 53 | 55.8 | 54.4 | 65.3 | 34.3 | 57.6 | 58 | 61.6 | 56.4 | 61 | 66.5
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 24 | 15 | 0 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 15 | 2.2 | 2.2 | [14 empty] | Muz | 384 | 400 | 427 | 411 | 439 | 397.7 | 72 | 20 | 95.1 | 405 | 425 | 430 | 421 | 511.4 | 480 | 505.1 | 479.1 | 481.1 | 229 | 94 | 306 | 366 | 380 | 397
DEVI(14.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 14.1 | 8.1 | 8.1 | [14 empty] | Ram | 52 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 35 | 37.2 | 40.7 | 41.6 | 34.3 | 2.3 | 3.7 | 3.4 | 51.6 | 48.2 | 51 | 55.5
MODI(14) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5.2 | 0 | [14 empty] | Rax | 102 | 106 | 120 | 110 | 110 | 108 | 70 | 0 | 44 | 0 | 40 | 88 | 76 | 63.8 | 81 | 80 | 73.6 | 0 | 0 | 108 | 100 | 100 | 53.8 | 107
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 51 | 53.8 | 50.4 | 49.9 | 46 | 50.3 | 78 | 75 | 71 | 69 | 74 | 71 | 67 | 61.8 | 58.2 | 68.5 | 64.9 | 75.9 | 71.8 | 65.2 | 68 | 69 | 67.5 | 58
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 58 | 55 | 54 | 52 | 55.4 | 64 | 53 | 60 | 63.3 | 62.8 | 51.8 | 45.8 | 48 | 53 | 55.8 | 54.4 | 65.3 | 34.3 | 57.6 | 58 | 61.6 | 56.4 | 61 | 66.5
Total ROR | 75.54 | 75.54 | 75.54 | 75.54 | 100.54 | 98.44 | 155.34 | 233.64 | 241.44 | 284.74 | 324.84 | 324.84 | 369.34 | 300.14 | 261.34 | 190.64 | 190.24 | 145.84 | 134.94 | 142.94 | 156.44 | 165.74 | 199.34 | 274.14 | 334.64 | 354.44 | 311.44 | 253.34 | 214.94 | 202.84 | 68.04 | 489.91 | 369.34 | 68.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.375: 50; 0.41667: 0; 0.72917: 60; 0.75: 60; 0.77083: 60; 0.79167: 60; 0.8125: 60; 0.83333: 0; 0.85417: 0; 0.875: 0 | 60 | 60 | 0 | [15 empty] | 384 | 400 | 427 | 411 | 439 | 397.7 | 72 | 20 | 95.1 | 405 | 425 | 430 | 421 | 511.4 | 480 | 505.1 | 479.1 | 481.1 | 229 | 94 | 306 | 366 | 380 | 397
KL2(32) | 0.375: 16.2; 0.41667: 0; 0.72917: 28; 0.75: 28; 0.77083: 28; 0.79167: 28; 0.8125: 28; 0.83333: 0; 0.85417: 0; 0.875: 0 | 32 | 28 | 0 | [15 empty] | 52 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 35 | 37.2 | 40.7 | 41.6 | 34.3 | 2.3 | 3.7 | 3.4 | 51.6 | 48.2 | 51 | 55.5
KL3(14) | 0.375: 5.9; 0.41667: 0; 0.72917: 10.2; 0.75: 10.2; 0.77083: 10.2; 0.79167: 10.2; 0.8125: 10.2; 0.83333: 0; 0.85417: 0; 0.875: 0 | 14 | 10.2 | 0 | [15 empty] | 102 | 106 | 120 | 110 | 110 | 108 | 70 | 0 | 44 | 0 | 40 | 88 | 76 | 63.8 | 81 | 80 | 73.6 | 0 | 0 | 108 | 100 | 100 | 53.8 | 107
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 0 | 0 | 0 | 0 | 0 | 106 | 98.2 | 0 | [15 empty] | 51 | 53.8 | 50.4 | 49.9 | 46 | 50.3 | 78 | 75 | 71 | 69 | 74 | 71 | 67 | 61.8 | 58.2 | 68.5 | 64.9 | 75.9 | 71.8 | 65.2 | 68 | 69 | 67.5 | 58
TANAKPUR | 66.5 | 57.9 | 55 | 54 | 52 | 55.4 | 63.8 | 64 | 47 | 53 | 54.3 | 60 | 63.3 | 62.8 | 51.8 | 45.8 | 48 | 53 | 55.8 | 54.4 | 65.3 | 56.3 | 34.3 | 52.2 | 57.6 | 68.5 | 58 | 56.5 | 61.6 | 56.4 | 61 |  | 68.5 | 34.3
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 397 | 383.8 | 400 | 427 | 411 | 439 | 459 | 397.7 | 415 | 72 | 4 | 20 | 95.1 | 405 | 425 | 430 | 421 | 511.4 | 480 | 505.1 | 479.1 | 477.3 | 481.1 | 394.6 | 229 | 95.1 | 94 | 299 | 306 | 366 | 380 |  | 511.4 | 4
RAMNAGAR | 55.5 | 52.3 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 40 | 35 | 37.2 | 40.7 | 41.6 | 34.3 | 1.5 | 2.3 | 3.5 | 3.7 | 3.89 | 3.4 | 3.1 | 51.6 | 48.2 | 51 |  | 55.5 | 0 | [22 empty] | 58 | 0 | 384 | 52 | 102 | 51
RAXAUL 132 | 107 | 102 | 106 | 120 | 110 | 110 | 108 | 108 | 110 | 70 | 0 |  | 44 | 0 | 40 | 88 | 76 | 63.8 | 81 | 80 | 73.6 | 0 | 0 | 0 | 0 | 0 | 108 | 96 | 100 | 100 | 53.8 |  | 120 | 0 | [22 empty] | 55 | 0 | 400 | 50 | 106 | 53.8
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 54 | 0 | 427 | 3 | 120 | 50.4
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 52 | 0 | 411 | 0 | 110 | 49.9
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 55.4 | 0 | 439 | 0 | 110 | 46
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 64 | 0 | 397.7 | 0 | 108 | 50.3
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 53 | 0 | 72 | 0 | 70 | 78
SAMPATIYA 132 kV | 58 | 50.7 | 53.8 | 50.4 | 49.9 | 46 | 51.5 | 50.3 | 80 | 78 | 75 | 75 | 71 | 69 | 74 | 71 | 67 | 61.8 | 58.2 | 68.5 | 64.9 | 71.1 | 75.9 | 78.3 | 71.8 | 68.6 | 65.2 | 56 | 68 | 69 | 67.5 |  | 80 | 46 | [22 empty] | 60 | 0 | 20 | 0 | 0 | 75
Total IMPORT | 684 | 646.7 | 664.8 | 654.4 | 622.9 | 650.4 | 682.3 | 620 | 652 | 273 | 133.3 | 155 | 297.4 | 536.8 | 590.8 | 674.8 | 647 | 727.2 | 715.7 | 749.6 | 717.2 | 606.2 | 593.6 | 528.6 | 362.1 | 236.09 | 328.6 | 510.6 | 587.2 | 639.6 | 613.3 | 0 | 749.6 | 133.3 | [22 empty] | 63.3 | 0 | 95.1 | 24 | 44 | 71
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 62.8 | 0 | 405 | 0 | 0 | 69
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 51.8 | 0 | 425 | 0 | 40 | 74
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 45.8 | 0 | 430 | 40 | 88 | 71
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 48 | 0 | 421 | 35 | 76 | 67
TOTAL SYSTEM LOAD (ACTUAL) | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1351.39 | 1458.19 | 1528.99 | 1437.29 | 1402.69 | 1424.39 | 1301.39 | 1304.79 | 1342.49 | 1353.39 | 1290.19 | 1310.99 | 1288.59 | 1330.59 | 1311.69 | 1308.19 | 1378.69 | 1538.49 | 1550.49 | 1509.28 | 1400.59 | 1369.29 | 1354.99 | 1395.29 | 1164.19 | 2231.81 | 1550.49 | 1164.19 | [22 empty] | 53 | 0 | 511.4 | 37.2 | 63.8 | 61.8
Interruption/Tripping | 0.29167: 150; 0.3125: 250; 0.33333: 260; 0.375: 260; 0.41667: 260; 0.70833: 100; 0.72917: 100; 0.75: 100; 0.77083: 100; 0.79167: 100; 0.8125: 100; 0.83333: 100 |  | 260 | 100 | [22 empty] | 55.8 | 0 | 480 | 40.7 | 81 | 58.2
TOTAL SYSTEM LOAD (EXPECTED) | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1351.39 | 1458.19 | 1528.99 | 1587.29 | 1652.69 | 1684.39 | 1561.39 | 1564.79 | 1342.49 | 1353.39 | 1290.19 | 1310.99 | 1288.59 | 1330.59 | 1411.69 | 1408.19 | 1478.69 | 1638.49 | 1650.49 | 1609.28 | 1500.59 | 1369.29 | 1354.99 | 1395.29 | 1164.19 | 1693.71 | 1684.39 | 1164.19 | [22 empty] | 54.4 | 0 | 505.1 | 41.6 | 80 | 68.5
TOTAL NATIONAL LOAD (ACTUAL) | 1258.29 | 1220.99 | 1239.09 | 1228.69 | 1222.19 | 1262.59 | 1351.39 | 1458.19 | 1528.99 | 1587.29 | 1652.69 | 1684.39 | 1561.39 | 1564.79 | 1342.49 | 1353.39 | 1290.19 | 1310.99 | 1288.59 | 1330.59 | 1411.69 | 1408.19 | 1478.69 | 1638.49 | 1650.49 | 1609.28 | 1500.59 | 1369.29 | 1354.99 | 1395.29 | 1164.19 |  | 1684.39 | 1164.19 | [22 empty] | 65.3 | 0 | 479.1 | 34.3 | 73.6 | 64.9
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 34.3 | 0 | 481.1 | 2.3 | 0 | 75.9
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 57.6 | 0 | 229 | 3.7 | 0 | 71.8
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58 | 0 | 94 | 3.4 | 108 | 65.2
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61.6 | 0 | 306 | 51.6 | 100 | 68
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 56.4 | 0 | 366 | 48.2 | 100 | 69
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 61 | 0 | 380 | 51 | 53.8 | 67.5
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 66.5 | 0 | 397 | 55.5 | 107 | 58
NET IMPORT | 684 | 646.7 | 664.8 | 654.4 | 622.9 | 650.4 | 682.3 | 620 | 652 | 273 | 133.3 | 155 | 297.4 | 536.8 | 590.8 | 674.8 | 647 | 727.2 | 715.7 | 749.6 | 717.2 | 606.2 | 593.6 | 528.6 | 362.1 | 236.09 | 328.6 | 510.6 | 587.2 | 639.6 | 613.3 |  | 749.6 | 133.3
HZ | 50.003 | 50.051 | 50.041 | 50.066 | 50 | 49.991 | 50.013 | 50.047 | 50.1 | 49.943 | 49.92 | 50.057 | 49.893 | 50.015 | 50.044 | 50.052 | 50.031 | 50.06 | 49.98 | 49.952 | 50.06 | 50.02 | 49.94 | 50.02 | 50.06 | 50 | 50.084 | 49.998 | 49.934 | 49.862 | 49.907 |  | 50.1 | 49.862
HTD 132KV | 130.7 | 130.5 | 131.1 | 128 | 128 | 128 | 128 | 126.9 | 126.9 | 128 | 126 | 129.2 | 130.5 | 125.7 | 124.7 | 125.6 | 127.4 | 124.6 | 125.5 | 124.2 | 124.2 | 125.8 | 125.8 | 126.5 | 127.8 | 127.8 | 129.7 | 129.4 | 131.8 | 130.6 | 132.1 |  | 132.1 | 124.2
SUI 132KV | 134.7 | 134.2 | 135.2 | 132 | 132 | 132 | 132 | 130 | 130 | 130 | 128.8 | 130.9 | 131.6 | 128.5 | 127.8 | 128.8 | 130.7 | 128.5 | 130 | 129 | 129 | 130.8 | 130.8 | 129.5 | 129.8 | 130.9 | 131.6 | 131.9 | 134.1 | 133.5 | 135.3 |  | 135.3 | 127.8
DUBI 132KV | 130 | 133.6 | 128.8 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126 | 124.8 | 126.5 | 127.3 | 126.4 | 123.9 | 129.6 | 128.3 | 123.1 | 129.3 | 126.3 | 126.3 | 131 | 131 | 125 | 127.8 | 130.5 | 132.1 | 131.8 | 128.5 | 127 | 130.3 |  | 133.6 | 123.1
ANAMANI 132KV | 132.5 | 131.4 | 132.3 | 130.6 | 130.6 | 130.6 | 130.6 | 128.6 | 128.6 | 125 | 123.4 | 122.9 | 124.2 | 124.8 | 122.8 | 129.9 | 128.2 | 120.5 | 129.3 | 126.8 | 126.8 | 129.9 | 129.9 | 124.1 | 127.1 | 129 | 132 | 132.3 | 129.6 | 129.3 | 133.1 |  | 133.1 | 120.5
KG-A 132KV | 133.8 | 133.3 | 134.5 | 132 | 132 | 132 | 132 | 131.9 | 131.9 | 136 | 134.6 | 135.5 | 135.2 | 134.2 | 132.6 | 133.8 | 135.5 | 132.5 | 135.8 | 134 | 134 | 136.3 | 136.3 | 136.7 | 136.2 | 137 | 136.3 | 136.4 | 137.2 | 135.2 | 137 |  | 137.2 | 131.9
KOHALPUR 132KV | 130.1 | 31.8 | 134.4 | 133 | 133 | 133 | 133 | 128 | 128 | 128 | 132 | 126.2 | 130.9 | 132.7 | 129.9 | 134.1 | 129.3 | 129.3 | 127.3 | 132.9 | 132.9 | 129.8 | 129.8 | 131.6 | 127.9 | 126.8 | 134.7 | 136.2 | 129.5 | 132.1 | 135.31 |  | 136.2 | 31.8
SUI 66KV | 67.5 | 67.4 | 67.8 | 66 | 66 | 66 | 65.8 | 65.4 | 65.4 | 65.2 | 64.1 | 65.5 | 65.9 | 64.3 | 64 | 64.6 | 65.6 | 64.6 | 65.4 | 65 | 65 | 65.6 | 65.6 | 65 | 64.1 | 65.4 | 66 | 66.1 | 67.3 | 67.1 | 68 |  | 68 | 64
[33 empty] | 0 | 0
Kathmandu Load | 155.663 | 140.159 | 131.177 | 135.34 | 44.44 | 66.54 | 75.98 | 89.74 | 113.64 | 126.74 | 314.34 | 325.14 | 327.92 | 313.94 | 42 | 228.5 | 247.34 | 235.8 | 230.8 | 232.874 | 229.8 | 238.52 | 265.7 | 318.3 | 335.3 | 320.8 | 295.04 | 257.94 | 264.24 | 213.1 | 142.14 |  | 335.3 | 42
MRS-SYU | -3.6 | -5.4 | -7.4 | -16.3 | -16.7 | -15 | -5.5 | 5.4 | 9.5 | 23.4 | 32.3 | 52.7 | 55 | 32.5 | 16.9 | 11 | 12.3 | 1.4 | 1.3 | 0.3 | 7.6 | 1.3 | 15.5 | 24.6 | 25.7 | 36.6 | 33.9 | 24.4 | 24.5 | 19.2 | -5.8 | 75 | 55 | -16.7
NMRS-MATA | -10.1 | -12.1 | -14.3 | -27 | [6 empty] | 46.2 | 73.9 | 76.8 | 45.6 | 17.4 | 5.2 | 7.1 | -5.5 | -5 | -5.8 | 6.4 | -2.2 | 20.7 | 31.9 | 32.9 | 48.3 | 44 | 29.2 | 24 | 19 | -15 | 240 | 76.8 | -27
KL2-MATA | -7.6 | -12.4 | -12.8 | -8.9 | -14.6 | 0 | 1.74 | 3 | 15 | 4 | 3.9 | 23.5 | 34.9 | 16 | 23 | -20.8 | 14 | 16.8 | 16 | 16.7 | 19 | 10 | 13 | 21 | 20 | 8 | 19 | 18 | 12 | 2.54 | 0 | 240 | 34.9 | -20.8
KL1-SYU | -3.6 | -8.5 | -5.2 | -8 | -9.8 | -2.2 | -4 | -2.9 | 4.6 | 13.7 | 14.5 | 28.2 | 30.6 | 16 | 4.4 | 3.9 | 0.3 | 0.3 | -2.6 | -1 | 2.7 | 31.5 | 10 | 30.3 | 43 | 35 | 11 | 6 | 13.2 | 4.9 | 2.7 | 60 | 43 | -9.8
KHIMTI-LAMOSANGHU | 95.023 | 93.019 | 85.337 | 110 | [6 empty] | 128 | 57.4 | 36.08 | 106.6 | 131.2 | 129.56 | 114.8 | 126.56 | 128.96 | 133.334 | 112.16 | 116.48 | 125.76 | 129.76 | 132.96 | 112.16 | 106.6 | 114.8 | 110 | 86.92 | 80 | 120 | 133.334 | 36.08
LAMOSHANGU-BHAKTAPUR | 70 | 68.1 | 64.1 | 76.2 | 74.8 | 82.4 | 84.9 | 86.6 | 94 | 84.8 | 85.3 | 47.2 | 36.9 | 68.2 | 83.8 | 82.9 | 78 | 82.8 | 83.9 | 87.3 | 76.8 | 78.8 | 85.9 | 87.5 | 88.3 | 78.3 | 75 | 80 | 71.2 | 66.3 | 68
BALAJU-SYUCHATAR | 46.2 | 49.1 | 49.3 | 66.9 | 78 | 64.5 | 53.7 | 40.8 | 27.4 | 2.5 | -5.5 | -65.7 | -75 | -22.8 | 18.4 | 29.1 | 28.7 | 43.4 | 42.7 | 42.8 | 23.3 | 31.6 | 16.7 | -1.3 | -2.3 | -13.2 | -17 | 1.4 | 2.6 | 10.8 | 46
DHALKE-NAWALPUR I | 75 | 71.5 | 70 | 82.7 | 85.5 | 93.4 | 89.8 | 90 | 96.2 | 69.7 | 73.1 | 79 | 11 | 67.9 | 86.2 | 90.4 | 87 | 95 | 88.7 | 99.9 | 81.7 | 90.2 | 102.1 | 97.7 | 89.3 | 72.5 | 53.6 | 76.9 | 65.6 | 61 | 71 |  | 102.1 | 11
N. BHARATPUR-BARDGHAT I | 12.1 | 10 | 10.4 | 26.6 | [6 empty] | 1.7 | -20.9 | -25.8 | -2.9 | -1 | -13 | -14.6 | -4.7 | -4.6 | 1.2 | -3.3 | 3.2 | 2.3 | 5.1 | 6 | 0 | 6.6 | 7.2 | 0 | 1.9 | 5 |  | 26.6 | -25.8
DAMAK-DUHABI | -14.9 | -12.4 | -12.7 | -12.5 | -13.4 | -17 | -22.3 | -32.8 | -40.8 | -45 | -47.9 | -49.4 | -45.8 | -39.9 | -37.9 | -27.6 | -30.8 | -27.9 | -29.2 | -33.1 | -45.7 | -45.3 | -54.2 | -64 | -59.9 | -48.9 | -41 | -33.4 | -31 | -20 | -17 |  | -12.4 | -64
HETAUDA-KAMANE | -18 | -16.1 | -16.8 | -26.4 | -28.2 | -32.8 | -28.5 | -25.7 | -29.7 | -7.5 | -1.5 | 9.8 | 18.1 | -5.5 | -33.3 | -22.3 | -21.3 | -31.1 | -28 | -31.7 | -31.1 | -9.4 | -15 | -3.4 | 5.2 | 26.4 | -13 | -21.4 | -12.8 | -10 | -19 |  | 26.4 | -33.3
MIRCHAIYA LAHAN 2 | 100.7 | 89.2 | 95 | 95.9 | [6 empty] | 101.9 |  | 96.8 | 98.2 | 102 | 109.6 | 105.4 | 109.5 | 108.5 | 112.7 | 115.9 | 113.1 | 95.5 | 117.7 | 112.6 | 101.6 | 93.6 | 97 | 97 | 104 | 92 |  | 117.7 | 89.2
Water Level
UTK | 1983.35 | 1983.6 | 1983.85 | 1984.1 | 1984.35 | 1984.52 |  | 1984.65 |  | 1984.39 |  | 1983.2 | 1982.52 | 1982.6 | 1982.89 | 1982.98 | 1983.08 | 1983.27 | 1983.48 | 1983.68 | 1983.9 |  | 1984.1 |  | 1983.95 |  | 1983 |  | 1982.74 | 1982.85 | 1983.1
KGA | 519.85 | 520.23 | 520.58 | 520.9 | 521.26 | 521.54 |  | 521.65 |  | 521.48 |  | 521.2 | 520.7 | 520.28 | 520.1 | 519.96 | 519.74 | 519.69 | 519.77 | 519.94 | 520.07 |  | 520.14 |  | 519.86 |  | 519.24 |  | 518.88 | 518.94 | 519.22
MMRS | 622.9 | 623.26 | 623.67 | 624.08 | 624.35 | 624.37 |  | 624.24 |  | 624.2 |  | 623.71 | 623.03 | 622.55 | 621.54 | 620.94 | 621.48 | 622.82 | 622.97 | 622.95 | 622.89 |  | 622.91 |  | 622.75 |  | 621.69 |  | 621.75 | 622 | 622.52
MRS | 334.75 | 334.99 | 335.29 | 335.57 | 335.84 | 336.06 |  | 336.12 |  | 335.86 |  | 335.43 | 334.87 | 334.32 | 334.03 | 333.85 | 334.29 | 334.86 | 335.34 | 335.94 | 336.37 |  | 336.56 |  | 336.42 |  | 335.9 |  | 335.39 | 334.86 | 334.8
CHM | 882.7 | 883.6 | 884.3 | 884.9 | 885.6 | 886 |  | 886.5 |  | 886.2 |  | 885.9 | 885.8 | 885.6 | 885.1 | 884.9 | 885.4 | 885.9 | 886.4 | 887 | 887.2 |  | 886.6 |  | 886 |  | 884.3 |  | 883.4 | 882.9 | 882.3
KL 1 | 0: 1519.74; 0.125: 1519.75; 0.70833: 1519.75; 0.8125: 1519.73
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1684.39; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/25)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 26
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/26 |  |  | 2080/10/26 |  |  | Saturday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 614.4 | 608.9 | 626.7 | 601.3 | 662.3 | 668.04 | 649.3 | 694.8 | 488.9 | 115.6 | 104.1 | 397 | 456.2 | 570 | 566 | 594.3 | 643 | 640.5 | 571.5 | 647.7 | 655.1 | 663 | 702.2 | 257.8 | 242.9 | 207.8 | 572.7 | 596.9 | 610.3 | 617.6 | 654
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1502MW at 9:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1155 | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1244.03 | 1320.49 | 1389.49 | 1467.99 | 1320.29 | 1471.49 | 1501.89 | 1397.59 | 1262.29 | 1255.89 | 1264.59 | 1319.19 | 1338.59 | 1358.68 | 1331.2 | 1349.4 | 1504.19 | 1676.35 | 1644.15 | 1663.19 | 1583.69 | 1545.69 | 1417.89 | 1287.69 | 1207.79
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1501.89 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1501.89 MW
Solu Khola Dudhkoshi(86) | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 23.6 | 21.2 | 24 | 21.8 | 21.8 | 21.8 | 26.1 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 22.4 | 22.4 | 22.4 | 25.8 | 25.8 | 25.7 | 25.1 | 25.7 | 86 | 26.1 | 20.6
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 26
Super Dordi (54) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 54 | 11 | 11 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/26)
Likhu-IV(52.4) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 52.4 | 14 | 13.2
Upper Marsyangdi "A"(50) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 25 | 0 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 45 | 15.4 | 12.9 |  | IPP | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 450.35 | 447.95 | 450.75 | 448.55
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 158 | 376.5 | 86.5 | 51.5 | 36.5
Mistri Khola(42) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 42 | 6 | 6 |  | NEA ROR PROR | 68.04 | 68.04 | 68.04 | 70.54 | 70.54 | 70.54 | 187.84 | 273.74 | 294.04 | 290.44 | 189.14 | 207.24
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 654 | 614.4 | 608.9 | 626.7 | 601.3 | 662.3 | 649.3 | 488.9 | 104.1 | 397 | 456.2 | 570
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 250 | 280 | 250 | 0
Nyadi(30) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 30 | 7.2 | 6.7 |  | System_Load | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1320.49 | 1467.99 | 1474.99 | 1501.89 | 1397.59 | 1262.29
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5 | 0 | 0 | 0
Lower Likhu(28) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 28 | 6.7 | 6.7 |  | National_Load | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1320.49 | 1467.99 | 1471.49 | 1501.89 | 1397.59 | 1262.29
Dordi(27) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 30 | 14.5 | 5.2
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 25 | 8.3 | 8.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 25 | 12.4 | 12.4
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 23.5 | 6.9 | 6.9
Upper Chaku A(22.2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 22 | 9.3 | 9.3
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 7.5 | 7.5
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 17.8 | 17.8 | 17.8 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 17.9 | 21.6 | 16.8 | 19.7 | 18.6 | 17.4 | 17.1 | 17.1 | 17.1 | 19.6 | 15.8 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 11.5 | 12.1 | 14.9 | 14.2 | 19 | 240 | 21.6 | 11.5
Total IPP | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 447.35 | 450.35 | 447.95 | 450.75 | 448.55 | 448.55 | 448.55 | 464.75 | 463.35 | 463.35 | 463.35 | 463.35 | 463.35 | 461.05 | 461.05 | 461.05 | 467.45 | 467.45 | 467.35 | 466.75 | 467.35 | 1042.4 | 467.45 | 447.35
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 330 | 340 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 55 | 55 | 105 | 380 | 380 | 390 | 60 | 40 | 30 | 15 | 456 | 390 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9 | 9 | 9 | 9 | 5.2 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 22.1 | 10.5 | 5.2
Total NEA SUBSIDIARIES | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 158 | 366 | 376.5 | 86.5 | 51.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 126.5 | 61 | 91 | 91 | 141 | 412.2 | 417.5 | 427.5 | 97.5 | 77.5 | 67.5 | 52.5 | 538.1 | 427.5 | 36
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.8 | 65 | 97 | 91 | 91.5 | 91.4 | 30 | 49.1 | 49.1 | 30.6 | 30.8 | 49.1 | 48.39 | 30.41 | 30.41 | 60 | 94.5 | 132 | 141.6 | 111.7 | 100.4 | 91.7 | 25 | 0 | 144 | 141.6 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 60 | 59.5 | 50.4 | 25.5 | 29.8 | 29.8 | 25.1 | 25 | 35.4 | 35.4 | 25.7 | 25.7 | 25.7 | 51.3 | 53.1 | 55.6 | 24.7 | 24.7 | 34.6 | 24.6 | 0 | 70 | 60 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 22.3 | 46.5 | 46 | 65 | 63 | 55.7 | 55.3 | 32.4 | 32.8 | 32.8 | 32.8 | 34.9 | 22.3 | 22.4 | 16.8 | 0 | 16.8 | 34.4 | 57.8 | 68.3 | 68 | 67.9 | 67.6 | 16.3 | 0 | 69 | 68.3 | 0
U Trisuli 3A(60) | 33 | 33 | 33 | 35.5 | 35.5 | 35.5 | 35.3 | 35.5 | 35.3 | 35.3 | 35.3 | 35.3 | 36 | 36 | 35.3 | 35.3 | 35.3 | 35.3 | 34.3 | 34.5 | 34.3 | 34.3 | 34.3 | 33 | 33.3 | 33.3 | 34.3 | 34.3 | 32.2 | 32.2 | 35.3 | 60 | 36 | 32.2
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 10.5 | 10.3 | 10.3 | 15 | 10 | 10 | 10 | 0 | 10 | 15 | 15 | 15 | 15 | 23.9 | 27.9 | 28 | 27.5 | 23.9 | 15 | 10 | 0 | 30 | 28 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 6.7 | 12 | 15.2 | 15.2 | 15.2 | 18.4 | 15.6 | 12.1 | 6.6 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18.4 | 0 | [14 empty] | Tanakpur | 48 | 51.6 | 55.3 | 56 | 56.5 | 60.7 | 51.6 | 43.5 | 57.3 | 48 | 45 | 36 | 37.1 | 45 | 46.2 | 45 | 53.2 | 51 | 65.8 | 62.4 | 63 | 56 | 65 | 50
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 15 | 2.2 | 2.2 | [14 empty] | Muz | 389 | 388 | 405 | 431 | 455 | 428.6 | 279 | -3.5 | 284 | 353 | 387 | 395 | 414 | 429 | 432 | 382 | 392.6 | 413 | 110 | 69 | 334 | 349 | 352 | 392
DEVI(14.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 14.1 | 8.1 | 8.1 | [14 empty] | Ram | 1 | 1.7 | 1.9 | 2.3 | 3.2 | 4 | 4.9 | 2.6 | 0 | 0 | 0 | -2.4 | -2 | -1.7 | 0.3 | 0 | 50.2 | 52 | 5.4 | 4 | 42.3 | 47.4 | 42.8 | 42
MODI(14) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | [14 empty] | Rax | 130 | 120 | 116 | 112 | 106 | 111 | 90 | 0 | 0 | 0 | 88 | 78 | 88 | 108 | 96 | 78 | 88 | 76 | 0 | 0 | 88.6 | 88.8 | 90.6 | 120
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 46 | 47.6 | 48.5 | 0 | 41.6 | 45 | 63.4 | 58 | 55.7 | 55.2 | 50 | 57 | 55.2 | 61 | 66 | 66.5 | 63.7 | 71 | 76.6 | 72.4 | 69 | 69.1 | 67.2 | 50
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 48 | 51.6 | 55.3 | 56 | 56.5 | 60.7 | 51.6 | 43.5 | 57.3 | 48 | 45 | 36 | 37.1 | 45 | 46.2 | 45 | 53.2 | 51 | 65.8 | 62.4 | 63 | 56 | 65 | 50
Total ROR | 68.04 | 68.04 | 68.04 | 70.54 | 70.54 | 70.54 | 92.64 | 187.84 | 211.34 | 273.74 | 295.74 | 294.04 | 290.44 | 189.14 | 207.24 | 207.24 | 187.24 | 176.64 | 198.24 | 197.33 | 159.15 | 140.95 | 186.84 | 272.1 | 341.1 | 361.84 | 301.24 | 286.24 | 276.14 | 143.14 | 70.34 | 489.91 | 361.84 | 68.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.79167: 45; 0.8125: 50; 0.83333: 50; 0.85417: 0 | 60 | 50 | 0 | [15 empty] | 389 | 388 | 405 | 431 | 455 | 428.6 | 279 | -3.5 | 284 | 353 | 387 | 395 | 414 | 429 | 432 | 382 | 392.6 | 413 | 110 | 69 | 334 | 349 | 352 | 392
KL2(32) | 0.79167: 20; 0.8125: 21.9; 0.83333: 21.8; 0.85417: 16 | 32 | 21.9 | 16 | [15 empty] | 1 | 1.7 | 1.9 | 2.3 | 3.2 | 4 | 4.9 | 2.6 | 0 | 0 | 0 | -2.4 | -2 | -1.7 | 0.3 | 0 | 50.2 | 52 | 5.4 | 4 | 42.3 | 47.4 | 42.8 | 42
KL3(14) | 0.79167: 7; 0.8125: 8; 0.83333: 7.9; 0.85417: 5.8 | 14 | 8 | 5.8 | [15 empty] | 130 | 120 | 116 | 112 | 106 | 111 | 90 | 0 | 0 | 0 | 88 | 78 | 88 | 108 | 96 | 78 | 88 | 76 | 0 | 0 | 88.6 | 88.8 | 90.6 | 120
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 79.9 | 79.7 | 21.8 | 0 | 0 | 0 | 106 | 79.9 | 0 | [15 empty] | 46 | 47.6 | 48.5 | 0 | 41.6 | 45 | 63.4 | 58 | 55.7 | 55.2 | 50 | 57 | 55.2 | 61 | 66 | 66.5 | 63.7 | 71 | 76.6 | 72.4 | 69 | 69.1 | 67.2 | 50
TANAKPUR | 50 | 48 | 51.6 | 55.3 | 56 | 56.5 | 60 | 60.7 | 61.3 | 51.6 | 52 | 43.5 | 57.3 | 48 | 45 | 36 | 37.1 | 45 | 46.2 | 45 | 53.2 | 53.2 | 51 | 63.5 | 65.8 | 68.2 | 62.4 | 58.4 | 63 | 56 | 65 |  | 68.2 | 36
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 392 | 389 | 388 | 405 | 431 | 455 | 461 | 428.6 | 443 | 279 | -4.4 | -3.5 | 284 | 353 | 387 | 395 | 414 | 429 | 432 | 382 | 392.6 | 400 | 413 | 439.8 | 110 | 97.1 | 69 | 331.9 | 334 | 349 | 352 |  | 461 | -4.4
RAMNAGAR | 42 | 1.4 | 1.7 | 1.9 | 2.3 | 3.2 | 3.3 | 4 | 4.6 | 4.9 | 4.6 | 2.6 | 0 |  |  | -2.4 | -2 | -1.7 | 0.3 | 0 | 50.2 | 50.2 | 52 | 50.1 | 5.4 | 4.9 | 4 | 44.4 | 42.3 | 47.4 | 42.8 |  | 52 | -2.4 | [22 empty] | 48 | 0 | 389 | 1 | 130 | 46
RAXAUL 132 | 120 | 130 | 120 | 116 | 112 | 106 | 96 | 111 | 112 | 90 | 0 |  | 0 |  | 88 | 78 | 88 | 108 | 96 | 78 | 88 | 88 | 76 | 72 | 0 | 0 | 0 | 71 | 88.6 | 88.8 | 90.6 |  | 130 | 0 | [22 empty] | 51.6 | 0 | 388 | 1.7 | 120 | 47.6
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 55.3 | 0 | 405 | 1.9 | 116 | 48.5
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 56 | 0 | 431 | 2.3 | 112 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 56.5 | 0 | 455 | 3.2 | 106 | 41.6
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 60.7 | 0 | 428.6 | 4 | 111 | 45
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 51.6 | 0 | 279 | 4.9 | 90 | 63.4
SAMPATIYA 132 kV | 50 | 46 | 47.6 | 48.5 | 0 | 41.6 | 47.74 | 45 | 73.9 | 63.4 | 59 | 58 | 55.7 | 55.2 | 50 | 57 | 55.2 | 61 | 66 | 66.5 | 63.7 | 63.7 | 71 | 76.8 | 76.6 | 72.7 | 72.4 | 67 | 69 | 69.1 | 67.2 |  | 76.8 | 0 | [22 empty] | 43.5 | 0 | -3.5 | 2.6 | 0 | 58
Total IMPORT | 654 | 614.4 | 608.9 | 626.7 | 601.3 | 662.3 | 668.04 | 649.3 | 694.8 | 488.9 | 115.6 | 104.1 | 397 | 456.2 | 570 | 566 | 594.3 | 643 | 640.5 | 571.5 | 647.7 | 655.1 | 663 | 702.2 | 257.8 | 242.9 | 207.8 | 572.7 | 596.9 | 610.3 | 617.6 | 0 | 702.2 | 104.1 | [22 empty] | 57.3 | 0 | 284 | 0 | 0 | 55.7
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 48 | 0 | 353 | 0 | 0 | 55.2
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 45 | 0 | 387 | 0 | 88 | 50
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 36 | 0 | 395 | -2.4 | 78 | 57
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 37.1 | 0 | 414 | -2 | 88 | 55.2
TOTAL SYSTEM LOAD (ACTUAL) | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1244.03 | 1320.49 | 1389.49 | 1367.99 | 1224.69 | 1224.99 | 1221.89 | 1147.59 | 1262.29 | 1258.29 | 1266.59 | 1320.89 | 1338.59 | 1358.68 | 1331.2 | 1350.4 | 1404.19 | 1576.35 | 1544.15 | 1563.19 | 1483.69 | 1445.69 | 1417.89 | 1287.69 | 1207.79 | 2231.81 | 1576.35 | 1147.59 | [22 empty] | 45 | 0 | 429 | -1.7 | 108 | 61
Interruption/Tripping | 0.29167: 100; 0.3125: 100; 0.33333: 250; 0.375: 280; 0.41667: 250; 0.75: 100; 0.77083: 100; 0.79167: 100; 0.8125: 100; 0.83333: 100; 0.85417: 100 |  | 280 | 100 | [22 empty] | 46.2 | 0 | 432 | 0.3 | 96 | 66
TOTAL SYSTEM LOAD (EXPECTED) | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1244.03 | 1320.49 | 1389.49 | 1467.99 | 1324.69 | 1474.99 | 1501.89 | 1397.59 | 1262.29 | 1258.29 | 1266.59 | 1320.89 | 1338.59 | 1358.68 | 1331.2 | 1350.4 | 1504.19 | 1676.35 | 1644.15 | 1663.19 | 1583.69 | 1545.69 | 1417.89 | 1287.69 | 1207.79 | 1693.71 | 1676.35 | 1155.19 | [22 empty] | 45 | 0 | 382 | 0 | 78 | 66.5
TOTAL NATIONAL LOAD (ACTUAL) | 1205.39 | 1165.79 | 1160.29 | 1180.59 | 1155.19 | 1216.19 | 1244.03 | 1320.49 | 1389.49 | 1467.99 | 1320.29 | 1471.49 | 1501.89 | 1397.59 | 1262.29 | 1255.89 | 1264.59 | 1319.19 | 1338.59 | 1358.68 | 1331.2 | 1349.4 | 1504.19 | 1676.35 | 1644.15 | 1663.19 | 1583.69 | 1545.69 | 1417.89 | 1287.69 | 1207.79 |  | 1676.35 | 1155.19 | [22 empty] | 53.2 | 0 | 392.6 | 50.2 | 88 | 63.7
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 2 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.4 | 0 | [22 empty] | 51 | 0 | 413 | 52 | 76 | 71
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 65.8 | 0 | 110 | 5.4 | 0 | 76.6
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 62.4 | 0 | 69 | 4 | 0 | 72.4
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.4 | 0 | [22 empty] | 63 | 0 | 334 | 42.3 | 88.6 | 69
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 56 | 0 | 349 | 47.4 | 88.8 | 69.1
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | [22 empty] | 65 | 0 | 352 | 42.8 | 90.6 | 67.2
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 3.5 | 0 | 0 | 0 | 2.4 | 2 | 1.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.4 | 0 | [22 empty] | 50 | 0 | 392 | 42 | 120 | 50
NET IMPORT | 654 | 614.4 | 608.9 | 626.7 | 601.3 | 662.3 | 668.04 | 649.3 | 694.8 | 488.9 | 111.2 | 100.6 | 397 | 456.2 | 570 | 563.6 | 592.3 | 641.3 | 640.5 | 571.5 | 647.7 | 654.1 | 663 | 702.2 | 257.8 | 242.9 | 207.8 | 572.7 | 596.9 | 610.3 | 617.6 |  | 702.2 | 100.6
HZ | 49.962 | 49.9746 | 49.976 | 50.051 | 49.978 | 49.991 | 49.976 | 50.016 | 50.1 | 50 | 50.086 | 50.065 | 49.946 | 50.067 | 50.017 | 50.102 | 49.98 | 50.0012 | 49.917 | 49.646 | 50.03 | 50.03 | 49.97 | 50.049 | 49.812 | 49.722 | 50.041 | 50.009 | 50.096 | 50.049 | 49.953 |  | 50.102 | 49.646
HTD 132KV | 129.1 | 128.4 | 129.5 | 129.5 | 129.5 | 129.5 | 125.6 | 129.7 | 129.7 | 130 | 128.5 | 127 | 127.6 | 127.5 | 125.2 | 124.6 | 124.6 | 124.7 | 126.6 | 126.6 | 126.6 | 126.6 | 128 | 127.5 | 127.7 | 127 | 131.6 | 130.7 | 130.9 | 130.9 | 130.6 |  | 131.6 | 124.6
SUI 132KV | 134 | 133.4 | 134.2 | 134.2 | 134.2 | 134.2 | 130 | 132 | 132 | 131.9 | 130.2 | 128.7 | 129.3 | 129.4 | 128.1 | 127.9 | 128 | 128.2 | 130 | 130 | 130 | 130 | 130 | 129.5 | 129 | 129.2 | 133.3 | 132.8 | 133.3 | 134.8 | 134.8 |  | 134.8 | 127.9
DUBI 132KV | 127.3 | 128.3 | 126.6 | 126.6 | 126.6 | 126.6 | 128.5 | 126 | 126 | 130.6 | 130 | 129.9 | 130.2 | 132.3 | 133.8 | 133.3 | 131.6 | 128.2 | 128.8 | 128.8 | 128.8 | 128.8 | 128 | 127.2 | 130.6 | 130.2 | 129.4 | 128.3 | 132.1 | 132.9 | 131.7 |  | 133.8 | 126
ANAMANI 132KV | 130.3 | 130.2 | 129.3 | 129.3 | 129.3 | 129.3 | 128.8 | 126.6 | 126.6 | 129 | 127.8 | 128.4 | 128.4 | 130.5 | 131.8 | 132.3 | 131.5 | 129.3 | 129.6 | 129.6 | 129.6 | 129.6 | 126 | 124.5 | 129.2 | 129.9 | 130.4 | 129.7 | 133.2 | 134.2 | 132.2 |  | 134.2 | 124.5
KG-A 132KV | 132.6 | 132 | 133.1 | 133.1 | 133.1 | 133.1 | 128.7 | 133 | 133 | 136 | 133.6 | 132.2 | 132.6 | 134 | 129.8 | 129.5 | 129.7 | 129.4 | 134.1 | 134.1 | 134.1 | 134.1 | 134.7 | 133.3 | 130.2 | 133.6 | 136.1 | 136.8 | 136.2 | 136.6 | 136 |  | 136.8 | 128.7
KOHALPUR 132KV | 134.1 | 131.7 | 130 | 130 | 130 | 130 | 136 | 135 | 135 | 129 | 128.5 | 128.5 | 130.2 | 134.9 | 132.6 | 135 | 132.5 | 134.6 | 134.6 | 134.6 | 134.6 | 134.6 | 136 | 134.2 | 123.7 | 131.6 | 134.1 | 130.4 | 135.7 | 135 | 132.2 |  | 136 | 123.7
SUI 66KV | 67.5 | 67.3 | 67.7 | 67.7 | 66 | 66 | 65.4 | 66.8 | 65.7 | 66 | 65.1 | 64.1 | 64.5 | 64.6 | 64.1 | 63.9 | 64.2 | 64.2 | 65.2 | 65.2 | 66 | 66 | 65.2 | 65 | 64.7 | 64.8 | 66.5 | 66.3 | 66.8 | 67.7 | 67.6 |  | 67.7 | 63.9
[33 empty] | 0 | 0
Kathmandu Load | 122.64 | 115.24 | 131.74 | 112.34 | 104.84 | 140.74 | 166.44 | 205.14 | 250.94 | 273.04 | 280.54 | 305.52 | 314.636 | 301.96 | 42 | 116.74 | 244.24 | 231.872 | 231.592 | 232.14 | 254.94 | 253.54 | 281.04 | 359.278 | 350.597 | 312.469 | 309.8 | 287.772 | 260.72 | 197.04 | 162.78 |  | 359.278 | 42
MRS-SYU | -13 | -33 | 0 | -22.9 | -28.9 | -25.9 | -20.8 | -0.6 | 11.2 | 33.9 | 29.8 | 29.1 | 33.6 | 14.3 | 7.1 | 3 | -0.1 | -1.7 | 2.4 | -1.3 | 17.7 | 17.7 | 21 | 39.2 | 34.1 | 35.4 | 34.1 | 39.4 | 41.9 | 9.1 | -1.3 | 75 | 41.9 | -33
NMRS-MATA | -24 | -20 | -34 | -35.2 | -45.8 | -40.4 | -32 | -6.6 | 8.9 | 47.7 | 40.8 | 40.2 | 46.3 | 18.8 | 3.9 | -3.1 | -7.5 | -9.4 | -3.7 | -6.1 | 17.3 | 17.3 | 18 | 50.8 | 41.9 | 44 | 41 | 46.6 | 50.6 | 6.9 | -7.6 | 240 | 50.8 | -45.8
KL2-MATA | -4 | -5 | -5 | -4.2 | -0.6 | 3.5 | 5.5 | 3 | 14 | 5 | 12 | 19.5 | 27.8 | 34 | 25.7 | 20 | 19 | 15 | 13.3 | 14.7 | 19.6 | 19.6 | 34 | 35 | 14.6 | -15 | 26.5 | 23.3 | 7 | 3.4 | -3.1 | 240 | 35 | -15
KL1-SYU | -1.6 | -2 | 0.5 | -3.1 | -7.6 | -4.2 | -3.8 | 1.6 | 4.3 | 13 | 16.1 | 17.6 | 19.8 | 16.7 | 1.5 | -0.9 | 0.7 | -3 | 0.5 | 2 | 2.4 | 2.4 | 7 | 22.1 | 38 | 36.6 | 35.6 | 9.1 | 10.4 | 5.5 | -2.1 | 60 | 38 | -7.6
KHIMTI-LAMOSANGHU | 85 | 95 | 90 | 95 | 105 | 125 | 135 | 125 | 130 | 90 | 98.4 | 109.88 | 91.896 | 119.72 | 131.28 |  | 131.2 | 133.332 | 125.952 | 135 | 115 | 115 | 120 | 122.578 | 132.097 | 131.429 | 88.56 | 85.332 | 68.88 | 90.2 | 91.84 | 120 | 135 | 68.88
LAMOSHANGU-BHAKTAPUR | 71 | 74 | 72 | 74.2 | 83.8 | 86 | 86.2 | 76.2 | 76.2 | 60.9 | 71 | 74.2 | 64.4 | 78.7 | 84.1 | 86.1 | 86 | 85.4 | 94.2 | 88.3 | 72.4 | 72.4 | 87 | 81.3 | 85.4 | 86.2 | 66.3 | 65.4 | 56.6 | 68.7 | 68.8 |  | 94.2 | 56.6
BALAJU-SYUCHATAR | 60 | 71 | 72 | 72.9 | 80 | 80 | 70.2 | 42 | 20.2 | -22.4 | -15 | -17.4 | -33.2 | 0.3 | 24.9 | 11.2 | 43.2 | -43.7 | 43.6 | 47.8 | 10.1 | 10.1 | 7.6 | -25.6 | -19.3 | -6.8 | 40.6 | -23.3 | -23.6 | 29 | 44.4 |  | 80 | -43.7
DHALKE-NAWALPUR I | 78 | 81 | 76 | 80.8 | 98.8 | 97.9 | 99.4 | 84.6 | 78.1 | 42.6 | 53 | 55.8 | 59.5 | 83 | 91.2 | 97.3 | 102 | 101.3 | 98.3 | 93.9 | 71.4 | 71.4 | 71.4 | 70 | 66 | 81.9 | 40.3 | 57.9 | 43.6 | 66 | 70 |  | 102 | 40.3
N. BHARATPUR-BARDGHAT I | 15 | 25 | 26 | 27.2 | 27.8 | 23 | 23 | 18.8 | 6.2 | -4.7 | -3.1 | -2.5 | -5.9 | 3.7 | 7.1 | 12.4 | 13.1 | 11.2 | 11.8 | 11.8 | 2 | 2 | 2 | -14.6 | 0 | -6.2 | -2.1 | -9.2 | -13.3 | 2.3 | 6.9 |  | 27.8 | -14.6
DAMAK-DUHABI | -12.5 | -10 | -8.8 | -10.2 | -10 | -15 | -20.7 | -28.2 | -38 | -46.4 | -49 | -42 | -34.7 | -34.2 | -34 | -31 | -23.6 | -25.8 | -28.3 | -35 | -38.1 | -38.1 | -38.1 | -63.5 | -53.4 | -47.2 | -39.3 | -36.3 | -28.4 | -23.4 | -15.1 |  | -8.8 | -63.5
HETAUDA-KAMANE | -23 | -27.5 | -24 | -32.2 | -43.9 | -45.9 | -38.7 | -27.4 | -25.2 | 3.2 | -3 | -6.9 | -11.8 | -31.2 | -42.4 | -41 | -39.4 | -34.2 | -34.8 | -33.9 | -27.3 | -27.3 | -27.3 | -17.7 | -8.6 | 14.1 | 6.8 | -4 | 7.8 | -16.5 | -18.2 |  | 14.1 | -45.9
MIRCHAIYA LAHAN 2 | 92 | 86 | 86 | 86.9 | 83 | 90.6 | 93.3 | 97.2 | 103 | 90.7 | 70 | 68.4 | 67.7 | 62.5 | 52.6 | 56.4 | 62.4 | 74.9 | 88.6 | 96.2 | 99.1 | 99.1 | 99.1 | 118.5 | 112.2 | 103.6 | 110.8 | 111.3 | 104.9 | 92 | 82.1 |  | 118.5 | 52.6
Water Level
UTK | 1983.4 | 1983.65 | 1983.9 | 1984.15 | 1984.35 | 1984.55 |  | 1984.8 |  | 1984.9 |  | 1984.22 | 1983.35 | 1983.42 | 1983.63 | 1983.85 | 1984.09 | 1984.28 | 1984.42 | 1984.45 |  |  | 1984.5 |  | 1984.3 |  | 1983.3 |  | 1982.92 | 1983.12 | 1983.3
KGA | 519.62 | 520 | 520.35 | 520.7 | 521.02 | 521.33 |  | 521.56 |  | 521.5 |  | 521.21 | 520.95 | 520.8 | 520.92 | 520.95 | 521.05 | 521.16 | 521.26 | 521.26 | 521.28 |  | 521.36 |  | 521.06 |  | 520.44 |  | 520.06 | 520 | 520.34
MMRS | 622.79 | 623.17 | 623.64 | 624.05 | 624.28 | 624.6 |  | 624.77 |  | 624.67 |  | 624.45 | 623.93 | 623.72 | 623.79 | 623.79 | 623.74 | 623.78 | 623.6 | 623.29 | 623.1 |  | 622.86 |  | 622.16 |  | 621.99 |  | 622.18 | 622.01 | 622.26
MRS | 334.93 | 335.54 | 336 | 336.34 | 336.6 | 336.78 |  | 336.66 |  | 336.52 |  | 336.07 | 335.69 | 335.24 | 335.05 | 334.77 | 335.52 | 334.73 | 334.98 | 335.19 | 335.31 |  | 335.57 | 335.64 | 335.58 |  | 335.17 |  | 334.7 | 334.53 | 334.83
CHM | 883.2 | 884 | 884.7 | 885.2 | 885.9 | 8886.8 |  | 887.1 |  | 887.1 |  | 887.1 | 887 | 886.9 | 886.9 | 886.8 | 886.8 | 887.1 |  | 887.4 | 887.2 |  | 886.8 |  | 885.7 |  | 884.1 |  | 882.6 | 882.5
KL 1 | 0: 1519.71; 0.125: 1519.72; 0.29167: 1519.73; 0.33333: 1519.73
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1501.89; 0.041667: 9:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/26)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 27
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/27 |  |  | 2080/10/27 |  |  | Sunday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 606.5 | 578.7 | 564.2 | 579.6 | 615.4 | 641.6 | 649.4 | 641.7 | 512.1 | 401.5 | 428.7 | 417.8 | 471.4 | 646.9 | 618.9 | 679.6 | 675.3 | 800.1 | 822 | 757.8 | 746.2 | 763 | 739.9 | 644.4 | 644.6 | 611.9 | 643.3 | 671.4 | 623.4 | 674.9 | 617.6
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1676MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1139 | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1254.19 | 1372.39 | 1461.49 | 1500.59 | 1646.99 | 1675.99 | 1597.09 | 1554.79 | 1500.59 | 1426.59 | 1472.59 | 1459.29 | 1523.23 | 1570.03 | 1483.19 | 1570.29 | 1625.49 | 1788.05 | 1787.25 | 1723.89 | 1596.89 | 1512.89 | 1502.69 | 1363.29 | 1279.89
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1675.99 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1675.99 MW
Solu Khola Dudhkoshi(86) | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 26.1 | 25 | 24 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24.7 | 24.7 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 86 | 26.1 | 21.8
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 27
Super Dordi (54) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9.5 | 9.5 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 11 | 9.5 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/27)
Likhu-IV(52.4) | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 12.9 | 12.9 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 52.4 | 13.5 | 12.9
Upper Marsyangdi "A"(50) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 25 | 25 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 15.5 | 15.5 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 45 | 16.9 | 12.9 |  | IPP | 467.35 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 466.65 | 465.65 | 463.45 | 463.45
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 52.5 | 37.5 | 37.5 | 37.5 | 37.5 | 33.6 | 33.6 | 95.6 | 277.2 | 236.2 | 166.2 | 86.3
Mistri Khola(42) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 42 | 6.5 | 6 |  | NEA ROR PROR | 70.34 | 70.34 | 70.34 | 70.04 | 70.34 | 70.04 | 186.64 | 245.14 | 263.44 | 247.44 | 253.74 | 303.94
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 617.6 | 606.5 | 578.7 | 564.2 | 579.6 | 615.4 | 649.4 | 512.1 | 428.7 | 417.8 | 471.4 | 646.9
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 180 | 240 | 230 | 200 | 0
Nyadi(30) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6 | 6.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 30 | 7.6 | 6.6 |  | System_Load | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1372.39 | 1500.59 | 1675.99 | 1597.09 | 1554.79 | 1500.59
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 5.4 | 5.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 28 | 6.7 | 5.4 |  | National_Load | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1372.39 | 1500.59 | 1675.99 | 1597.09 | 1554.79 | 1500.59
Dordi(27) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 0 | 0 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 30 | 9.3 | 0
Upper Madi(25) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 6.3 | 6.3 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 25 | 8.7 | 6.3
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 25 | 12.4 | 6.4
Solu Khola(23.5) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 23.5 | 6.9 | 6
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 0
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 5.1 | 5.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 22 | 9.3 | 5.1
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 7.5 | 7.5
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 19.4 | 19.5 | 19.3 | 20.9 | 20.3 | 20.5 | 20.5 | 19.3 | 18.6 | 19.4 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 16 | 14.5 | 14.5 | 14.5 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 240 | 20.9 | 14.5
Total IPP | 467.35 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 467.75 | 466.65 | 465.65 | 463.45 | 463.45 | 463.45 | 463.45 | 454.45 | 454.45 | 454.45 | 454.45 | 447.95 | 447.95 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 1042.4 | 467.75 | 447.95
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 230 | 241 | 200 | 130 | 50 | 30 | 35 | 35 | 30 | 30 | 30 | 50 | 50 | 120 | 160 | 140 | 120 | 55 | 25 | 25 | 0 | 456 | 241 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 6.6 | 6.6 | 6.6 | 8.5 | 8.6 | 8.5 | 9.2 | 9.2 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.5 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 22.1 | 11.2 | 6.6
Total NEA SUBSIDIARIES | 52.5 | 37.5 | 37.5 | 37.5 | 37.5 | 33.6 | 33.6 | 33.6 | 70.5 | 95.6 | 265.5 | 277.2 | 236.2 | 166.2 | 86.3 | 66.3 | 71.3 | 71.3 | 66.2 | 66.2 | 66.2 | 86.2 | 86.2 | 157.5 | 198.2 | 178.2 | 158.2 | 93.2 | 63.2 | 63.2 | 38.2 | 538.1 | 277.2 | 33.6
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.1 | 61.2 | 61.2 | 71.1 | 81.2 | 61.8 | 48.7 | 81.5 | 61 | 61 | 61 | 48.7 | 87 | 80 | 71.6 | 80 | 110 | 133 | 106.9 | 91.4 | 90.9 | 90.9 | 60.9 | 0 | 144 | 133 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 25.2 | 35.6 | 51.6 | 46.3 | 45.5 | 46.3 | 46.3 | 46.2 | 47.5 | 47.5 | 47.5 | 47.5 | 34.9 | 24.9 | 24.9 | 0 | 30 | 49.4 | 53 | 48.5 | 23.8 | 23.8 | 24 | 24 | 24 | 70 | 53 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38.6 | 51.4 | 50.4 | 62.8 | 50.2 | 49.7 | 49.5 | 56.4 | 56.4 | 34.3 | 34.3 | 21.7 | 22.3 | 22.3 | 22.3 | 22.3 | 60 | 60.9 | 60.7 | 55.3 | 55.4 | 46.9 | 35.5 | 0 | 69 | 62.8 | 0
U Trisuli 3A(60) | 35.3 | 35.3 | 35.3 | 35 | 35.3 | 35 | 35 | 35.3 | 37.3 | 36.3 | 35.3 | 33.3 | 33.3 | 33.5 | 34 | 34 | 34 | 34 | 34.5 | 35.5 | 35.5 | 34.3 | 34.3 | 34 | 33 | 34.3 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 60 | 37.3 | 33
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.9 | 9.6 | 9.9 | 10.3 | 22.6 | 28.5 | 23 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 10 | 22.6 | 23.4 | 14.5 | 14.5 | 14.5 | 14.5 | 0 | 30 | 28.5 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.9 | 7.5 | 11 | 14.9 | 17.7 | 17.7 | 17.3 | 17.3 | 11.54 | 11.54 | 0.9 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17.7 | 0 | [14 empty] | Tanakpur | 54 | 40 | 52.8 | 61.7 | 42.2 | 44.7 | 44.4 | 64.3 | 53.6 | 48.5 | 45 | 54 | 49.3 | 56 | 52.4 | 64 | 65.8 | 63 | 56.5 | 64.4 | 60.1 | 49.1 | 55.8 | 65
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 2.2 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 0 | [14 empty] | Muz | 390 | 380.7 | 389.5 | 397.7 | 415.8 | 419 | 391 | 294.7 | 298.2 | 355.6 | 430 | 387 | 450 | 493 | 508.5 | 510 | 484 | 480 | 381 | 353.7 | 411.7 | 351.2 | 406.6 | 354
DEVI(14.1) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 8.1 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 14.1 | 11.4 | 8.1 | [14 empty] | Ram | 2 | 0 | 4.1 | 4 | 4.3 | 5.5 | 4.5 | 4.8 | 4 | 1.7 | 0.9 | 0.9 | 2.3 | 0.6 | 59.2 | 60 | 50 | 52 | 39.9 | 39.8 | 47.3 | 46.8 | 48.3 | 50
MODI(14) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | [14 empty] | Rax | 110 | 108 | 117.8 | 116.2 | 107 | 106.6 | 0 | 0 | 0 | 0 | 99 | 105 | 106 | 53.7 | 108 | 116 | 88 | 98 | 96 | 81.8 | 81.2 | 110.4 | 120.2 | 100
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 50 | 50 | 0 | 0 | 46.1 | 73.6 | 72.2 | 64.9 | 62 | 65.6 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 70 | 71 | 72.2 | 71.1 | 65.9 | 44 | 48
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 3.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.5 | [15 empty] | 54 | 40 | 52.8 | 61.7 | 42.2 | 44.7 | 44.4 | 64.3 | 53.6 | 48.5 | 45 | 54 | 49.3 | 56 | 52.4 | 64 | 65.8 | 63 | 56.5 | 64.4 | 60.1 | 49.1 | 55.8 | 65
Total ROR | 70.34 | 70.34 | 70.34 | 70.04 | 70.34 | 70.04 | 111.24 | 186.64 | 246.54 | 245.14 | 262.24 | 263.44 | 247.44 | 253.74 | 303.94 | 277.94 | 258.24 | 258.24 | 187.48 | 217.38 | 204.74 | 169.94 | 208.34 | 304.5 | 337.5 | 314.94 | 260.64 | 260.24 | 251.94 | 210.54 | 99.64 | 489.91 | 337.5 | 70.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.79167: 14 | 60 | 14 | 14 | [15 empty] | 390 | 380.7 | 389.5 | 397.7 | 415.8 | 419 | 391 | 294.7 | 298.2 | 355.6 | 430 | 387 | 450 | 493 | 508.5 | 510 | 484 | 480 | 381 | 353.7 | 411.7 | 351.2 | 406.6 | 354
KL2(32) | 0.79167: 5.1 | 32 | 5.1 | 5.1 | [15 empty] | 2 | 0 | 4.1 | 4 | 4.3 | 5.5 | 4.5 | 4.8 | 4 | 1.7 | 0.9 | 0.9 | 2.3 | 0.6 | 59.2 | 60 | 50 | 52 | 39.9 | 39.8 | 47.3 | 46.8 | 48.3 | 50
KL3(14) | 0.79167: 1.9 | 14 | 1.9 | 1.9 | [15 empty] | 110 | 108 | 117.8 | 116.2 | 107 | 106.6 | 0 | 0 | 0 | 0 | 99 | 105 | 106 | 53.7 | 108 | 116 | 88 | 98 | 96 | 81.8 | 81.2 | 110.4 | 120.2 | 100
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 21 | 0 | [15 empty] | 50 | 50 | 0 | 0 | 46.1 | 73.6 | 72.2 | 64.9 | 62 | 65.6 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 70 | 71 | 72.2 | 71.1 | 65.9 | 44 | 48
TANAKPUR | 65 | 54 | 40 | 52.8 | 61.7 | 42.2 | 40 | 44.7 | 40 | 44.4 | 47.1 | 64.3 | 53.6 | 48.5 | 45 | 54 | 49.3 | 56 | 52.4 | 64 | 65.8 | 61.6 | 63 | 53 | 56.5 | 49.7 | 64.4 | 62.7 | 60.1 | 49.1 | 55.8 |  | 65.8 | 40
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 354 | 390.4 | 380.7 | 389.5 | 397.7 | 415.8 | 445 | 419 | 420 | 391 | 280 | 294.7 | 298.2 | 355.6 | 430 | 387 | 450 | 493 | 508.5 | 510 | 484 | 469 | 480 | 472 | 381 | 385 | 353.7 | 398.4 | 411.7 | 351.2 | 406.6 |  | 510 | 280
RAMNAGAR | 50 | 2 | 0 | 4.1 | 4 | 4.3 | 4.6 | 5.5 | 6.5 | 4.5 | 5.6 | 4.8 | 4 | 1.7 | 0.9 | 0.9 | 2.3 | 0.6 | 59.2 | 60 | 50 | 54.6 | 52 | 38.9 | 39.9 | 39.9 | 39.8 | 35.4 | 47.3 | 46.8 | 48.3 |  | 60 | 0 | [22 empty] | 54 | 0 | 390 | 2 | 110 | 50
RAXAUL 132 | 100 | 110 | 108 | 117.8 | 116.2 | 107 | 103 | 106.6 | 100 | 0 | 0 | 0 | 0 | 0 | 99 | 105 | 106 | 53.7 | 108 | 116 | 88 | 91 | 98 | 106 | 96 | 100 | 81.8 | 74.6 | 81.2 | 110.4 | 120.2 |  | 120.2 | 0 | [22 empty] | 40 | 0 | 380.7 | 0 | 108 | 50
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 52.8 | 0 | 389.5 | 4.1 | 117.8 | 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 61.7 | 0 | 397.7 | 4 | 116.2 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 42.2 | 0 | 415.8 | 4.3 | 107 | 46.1
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 44.7 | 0 | 419 | 5.5 | 106.6 | 73.6
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 44.4 | 0 | 391 | 4.5 | 0 | 72.2
SAMPATIYA 132 kV | 48 | 50.1 | 50 | 0 | 0 | 46.1 | 49 | 73.6 | 75.2 | 72.2 | 68.8 | 64.9 | 62 | 65.6 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 71 | 70 | 72.2 | 72.2 | 71.1 | 65.9 | 44 |  | 75.2 | 0 | [22 empty] | 64.3 | 0 | 294.7 | 4.8 | 0 | 64.9
Total IMPORT | 617.6 | 606.5 | 578.7 | 564.2 | 579.6 | 615.4 | 641.6 | 649.4 | 641.7 | 512.1 | 401.5 | 428.7 | 417.8 | 471.4 | 646.9 | 618.9 | 679.6 | 675.3 | 800.1 | 822 | 757.8 | 746.2 | 763 | 739.9 | 644.4 | 644.6 | 611.9 | 643.3 | 671.4 | 623.4 | 674.9 | 0 | 822 | 401.5 | [22 empty] | 53.6 | 0 | 298.2 | 4 | 0 | 62
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 48.5 | 0 | 355.6 | 1.7 | 0 | 65.6
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 45 | 0 | 430 | 0.9 | 99 | 72
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 54 | 0 | 387 | 0.9 | 105 | 72
Total THERMAL | 0.75: 0 | 55.4 | 0 | 0 | [22 empty] | 49.3 | 0 | 450 | 2.3 | 106 | 72
TOTAL SYSTEM LOAD (ACTUAL) | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1254.19 | 1337.39 | 1426.49 | 1320.59 | 1396.99 | 1435.99 | 1367.09 | 1354.79 | 1500.59 | 1426.59 | 1472.59 | 1459.29 | 1508.23 | 1560.03 | 1483.19 | 1450.29 | 1505.49 | 1668.05 | 1667.25 | 1603.89 | 1496.89 | 1462.89 | 1452.69 | 1363.29 | 1278.89 | 2231.81 | 1668.05 | 1139.49 | [22 empty] | 56 | 0 | 493 | 0.6 | 53.7 | 72
Interruption/Tripping | [7 empty] | 35 | 35 | 180 | 250 | 240 | 230 | 200 |  |  |  |  | 15 | 10 |  | 120 | 120 | 120 | 120 | 120 | 100 | 50 | 50 | 0 | 1 |  | 250 | 0 | [22 empty] | 52.4 | 0 | 508.5 | 59.2 | 108 | 72
TOTAL SYSTEM LOAD (EXPECTED) | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1254.19 | 1372.39 | 1461.49 | 1500.59 | 1646.99 | 1675.99 | 1597.09 | 1554.79 | 1500.59 | 1426.59 | 1472.59 | 1459.29 | 1523.23 | 1570.03 | 1483.19 | 1570.29 | 1625.49 | 1788.05 | 1787.25 | 1723.89 | 1596.89 | 1512.89 | 1502.69 | 1363.29 | 1279.89 | 1693.71 | 1788.05 | 1139.49 | [22 empty] | 64 | 0 | 510 | 60 | 116 | 72
TOTAL NATIONAL LOAD (ACTUAL) | 1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1254.19 | 1372.39 | 1461.49 | 1500.59 | 1646.99 | 1675.99 | 1597.09 | 1554.79 | 1500.59 | 1426.59 | 1472.59 | 1459.29 | 1523.23 | 1570.03 | 1483.19 | 1570.29 | 1625.49 | 1788.05 | 1787.25 | 1723.89 | 1596.89 | 1512.89 | 1502.69 | 1363.29 | 1279.89 |  | 1788.05 | 1139.49 | [22 empty] | 65.8 | 0 | 484 | 50 | 88 | 70
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 63 | 0 | 480 | 52 | 98 | 70
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 56.5 | 0 | 381 | 39.9 | 96 | 71
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 64.4 | 0 | 353.7 | 39.8 | 81.8 | 72.2
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 60.1 | 0 | 411.7 | 47.3 | 81.2 | 71.1
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 49.1 | 0 | 351.2 | 46.8 | 110.4 | 65.9
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 55.8 | 0 | 406.6 | 48.3 | 120.2 | 44
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 65 | 0 | 354 | 50 | 100 | 48
NET IMPORT | 617.6 | 606.5 | 578.7 | 564.2 | 579.6 | 615.4 | 641.6 | 649.4 | 641.7 | 512.1 | 401.5 | 428.7 | 417.8 | 471.4 | 646.9 | 618.9 | 679.6 | 675.3 | 800.1 | 822 | 757.8 | 746.2 | 763 | 739.9 | 644.4 | 644.6 | 611.9 | 643.3 | 671.4 | 623.4 | 674.9 |  | 822 | 401.5
HZ | 50.026 | 49.962 | 49.979 | 49.976 | 49.994 | 50.031 | 49.943 | 49.986 | 50.145 | 50.035 | 50.035 | 49.985 | 49.988 | 50.04 | 50.034 | 50.007 | 49.934 | 50.1 | 50.035 | 49.82 | 50.032 | 49.994 | 50.015 | 49.99 | 50 | 49.974 | 50.06 | 50.04 | 50.04 | 50.01 | 49.98 |  | 50.145 | 49.82
HTD 132KV | 131.9 | 127.3 | 128.5 | 127 | 128.7 | 128 | 128.7 | 128.7 | 127.2 | 127.7 | 124.6 | 123.1 | 124.2 | 123.4 | 124 | 125.3 | 126.1 | 124 | 124 | 123 | 126 | 126 | 126 | 126 | 126 | 126 | 128.5 | 128.3 | 128.4 | 128.4 | 128.4 |  | 131.9 | 123
SUI 132KV | 135 | 131.7 | 133.3 | 131.7 | 133.1 | 132.4 | 132.8 | 132.5 | 130.7 | 130.2 | 127.6 | 126.3 | 127.7 | 127.2 | 128 | 128.8 | 128.9 | 127.7 | 128 | 127 | 129 | 129 | 129 | 129 | 129 | 129 | 131.5 | 131.7 | 131.9 | 131.9 | 131.9 |  | 135 | 126.3
DUBI 132KV | 132.7 | 130.7 | 131.3 | 130.9 | 130.6 | 130.3 | 126.3 | 128 | 123.8 | 128 | 125.8 | 125.4 | 125.8 | 126.5 | 123 |  |  |  |  | 122.6 | 128 | 128 | 128 | 128 | 128 | 128 | 130.9 | 128.4 | 128 | 128 | 128 |  | 132.7 | 122.6
ANAMANI 132KV | 133.3 | 131.8 | 132 | 132.3 | 131.8 | 131.7 | 130.2 | 129.2 | 124.2 | 127.8 | 123.7 | 121.8 | 122.9 | 124.2 | 122.5 | 125.7 | 127.1 | 128 | 124.6 | 122 | 127 | 127 | 126 | 126 | 126 | 126 | 130.8 | 129.3 | 129.5 | 129.5 | 129.5 |  | 133.3 | 121.8
KG-A 132KV | 135.5 | 129.4 | 133.4 | 127.6 | 135 | 132.1 | 132.4 | 135.2 | 134.3 | 135.3 | 132.9 | 131.3 | 133.1 | 132.4 | 131.6 | 132.6 | 133.1 | 131.5 | 136.5 | 133 | 135 | 135 | 135.5 | 135.5 | 135.5 | 135.5 | 136.5 | 137.1 | 133.9 | 133.9 | 133.9 |  | 137.1 | 127.6
KOHALPUR 132KV | 130.6 | 132.6 | 134 | 134.1 | 129.7 | 133.8 | 136.5 | 135.6 | 132.9 | 127.7 | 127.7 | 130.4 | 126.9 | 131.4 | 135.2 | 130 | 129.7 | 125 | 134 | 125 | 136 | 136 | 131 | 131 | 131 | 131 | 131.6 | 132.4 | 132.4 | 132.4 | 132.4 |  | 136.5 | 125
SUI 66KV | 68.2 | 66.3 | 67 | 66.2 | 67 | 66.7 | 66.7 | 66.5 | 65.4 | 65.1 | 63.9 | 63.4 | 64.1 | 63.8 | 64.3 | 64.6 | 64.6 | 64 | 63.9 | 63.9 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 66.2 | 66.4 | 66.4 | 66.4 |  | 68.2 | 63.4
[33 empty] | 0 | 0
Kathmandu Load | 140.26 | 135.62 | 130.78 | 126.14 | 125.768 | 150.722 | 184.246 | 219.978 | 272.39 | 301.428 | 332.24 | 340.575 | 322.411 | 326.487 | 42 | 301.94 | 287.94 | 259.84 | 299.98 | 298.58 | 300.74 | 306.14 | 332.24 | 399.4 | 389.1 | 369.54 | 331.04 | 310.48 | 279.04 | 212.2 | 155.3 |  | 399.4 | 42
MRS-SYU | -4.4 | -19.2 | -17.7 | -23.3 | -32.8 | -17.1 | -7.9 | 8.9 | 16.6 | 20.4 | 23 | 28.3 | 27.8 | 26.3 | 29 | 28 | 20.4 | 16 | 19.7 | 23.9 | 12.9 | 12.7 | 18 | 36.6 | 38 | 37.1 | 32.7 | 35.4 | 33 | 20.3 | -5.6 | 75 | 38 | -32.8
NMRS-MATA | -10.1 | -29.7 | -28.6 | -35.4 | -20 | -27.2 | -14.4 | 7.1 | 15.6 | 27.6 | 31.6 | 40 | 39.9 | 37.4 | 35.4 | 34 | 23.5 | 16 | 21.1 | 26.6 | 15 | 13.2 | 22 | 45.9 | 48.6 | 46.5 | 40 | 43.3 | 39.4 | 22.2 | -6.6 | 240 | 48.6 | -35.4
KL2-MATA | -8.3 | -3.5 | -6.2 | -5.8 | -6.2 | -2 | 6.3 | 7.4 | 17.2 | 23.1 | 25 | 19.4 | 14 | 11.4 | 13 | 17 | 15 | 14 | 22.6 | 20 | 35 | 36 | 42 | 41 | 40 | 34.5 | 30 | 25 | 15 | -3 | -8.6 | 240 | 42 | -8.6
KL1-SYU | -0.7 | -6.9 | -10 | -8.2 | -7.2 | -4.1 | 7.6 | 9.5 | 13.7 | 16.8 | 18 | 11.2 | 10.9 | 9.5 | 1.1 | 3 | 6.3 | 2.5 | -1.5 | 1 | 6.4 | 6.4 | 12.4 | 21.6 | 14.5 | 13.2 | 11.1 | 8.9 | 6.4 | 0.9 | -6.1 | 60 | 21.6 | -10
KHIMTI-LAMOSANGHU | 78.72 | 109.88 | 108.24 | 114.1 | 106.928 | 116.382 | 107.906 | 102.038 | 122.25 | 126.488 | 146.7 | 151.135 | 135.771 | 140.447 | 119.238 | 115.2 | 118.4 | 110 | 142 | 130 | 145 | 150 | 150 | 160 | 158 | 150 | 128.8 | 109.44 | 96.8 | 83.36 | 93.76 | 120 | 160 | 78.72
LAMOSHANGU-BHAKTAPUR | 63.1 | 77 | 76.4 | 80.3 | 78.1 | 81.1 | 77.1 | 73 | 81.5 | 84.5 | 94.1 | 93.1 | 86.4 | 87.8 | 78.1 | 78 | 81.4 | 86 | 87.4 | 86 | 91.4 | 95.4 | 96 | 96.1 | 98 | 92.1 | 86.6 | 77.1 | 70.8 | 64.4 | 70.5
BALAJU-SYUCHATAR | 45.4 | 66 | 66.8 | 75.6 | 69.4 | 60.8 | 50.6 | 24.3 | 15.8 | 0.9 | 0.8 | -0.9 | -1 | 96.7 | 3.4 | 6 | 19 | 27 | 20.1 | 13.6 | 15.8 | 18.3 | 7 | -19.1 | -20 | -17.2 | -8.2 | -13.6 | -7.4 | 14.9 | 48
DHALKE-NAWALPUR I | 62 | 87 | 84.9 | 92.2 | 87.4 | 92.2 | 86 | 74.4 | 79.9 | 88.8 | 92.4 | 100.2 | 85.8 | 95.5 | 77.5 | 83 | 86 | 94 | 96.1 | 91 | 100 | 104 | 104 | 95.9 | -50.4 | 89.4 | 81.1 | 72.6 | 65.2 | 57.4 | 74.9 |  | 104 | -50.4
N. BHARATPUR-BARDGHAT I | 9.9 | 30.1 | -29.6 | 26.3 | 23.4 | 18.9 | 19.3 | 8.7 | 6.9 | 5.6 | 3.4 | -4.7 | -3.6 | -1.5 | -3.4 | 2 | 3.3 | 5 | -4.2 | -10 | 0 | 0 | -2.4 | -12.6 | -13 | -9.6 | -9.2 | -10.9 | -14.8 | -2.1 | 14.9 |  | 30.1 | -29.6
DAMAK-DUHABI | -12.7 | -11.2 | -11.1 | -8.5 | -9.4 | -14.2 | -20.1 | -29.9 | -39.3 | -44.9 | -48 | -52.2 | -45.9 | -39.6 | -33.5 |  |  |  |  | -42 | -47.2 | -50.1 | -57 | -63.4 | -50.4 | -47.7 | -40.8 | -38.2 | -31.1 | -23.7 | -18.2 |  | -8.5 | -63.4
HETAUDA-KAMANE | -12.3 | -32.5 | -32 | -35.9 | -31.5 | -33.5 | -26.4 | -15.7 | 20.2 | -20.6 | -21.5 | -17.1 | -12.7 | -13.2 | -19.8 | -24 | -21.7 | -26 | -27.5 | -22 | -38.5 | -41.8 | -41 | -30.2 | -32.6 | -29.8 | -26.6 | -19.2 | -11.4 | -4 | -18.2 |  | 20.2 | -41.8
MIRCHAIYA LAHAN 2 | 83.2 | 78.5 | 77.5 | 74.6 | 80 | 77.1 | 91.3 | 95.1 | 108.2 | 102.4 | 108 | 112.7 | 107.5 | 103 | 125 | 76.2 | 121 | 116 | 125.5 | 128 | 115 | 104.8 | 111 | 125.5 | 115.6 | 112.5 | 110.9 | 117..3 | 118.5 | 110.7 | 96.1 |  | 128 | 74.6
Water Level
UTK | 1983.58 | 1983.82 | 1984.08 | 1984.3 | 1984.5 | 1984.7 |  | 1984.9 |  | 1984.98 |  | 1984.52 | 1984 | 1983.65 | 1983.59 | 1983.61 | 1983.78 | 1983.84 | 1983.9 | 1984.02 | 1984.11 |  | 1984.21 |  | 1984.1 |  | 1983.85 |  | 1983.9 | 1984 | 1984.22
KGA | 520.68 | 521.02 | 521.32 | 521.62 | 521.92 | 522.21 |  | 522.43 |  | 522.4 |  | 522.28 | 522.15 | 522.12 | 522.17 | 522.1 | 522.04 | 522.1 | 522.07 | 521.91 | 521.74 |  | 521.64 |  | 521.26 |  | 520.86 |  | 520.58 | 520.35 | 520.45
MMRS | 622.75 | 623.14 | 623.42 | 623.78 | 624.1 | 624.5 |  | 624.49 |  | 624.35 |  | 624 | 623.87 | 623.57 | 623.3 | 623.02 | 622.6 | 622.24 | 622.07 | 622.16 | 622.52 |  | 622.74 |  | 622.26 |  | 622.11 |  | 622.21 | 622.24 | 622.31
MRS | 335.15 | 335.72 | 335.94 | 336.23 | 336.54 | 336.8 |  | 336.85 |  | 336.63 |  | 336.25 | 335.85 | 335.49 | 335.09 | 334.59 |  | 334.37 | 334.5 | 334.82 | 335.1 |  | 335.39 |  | 335.42 |  | 335.2 |  | 334.99 | 334.82 | 334.97
CHM | 883.9 | 884.6 | 885.3 | 885.9 | 886.5 | 886.9 |  | 887.2 |  | 887.4 |  | 887.3 | 887.3 | 887.1 | 886.1 | 885.6 | 884.4 | 882.5 | 883.3 |  | 884.5 |  | 885.1 |  | 884.7 |  | 883.9 |  | 883.6 | 883.1 | 883.5
KL 1 | 0.33333: 1519.72; 0.41667: 1519.72; 0.79167: 1519.73
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1675.99; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/27)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 28
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/28 |  |  | 2080/10/28 |  |  | Monday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 581.55 | 579.18 | 600.17 | 593.2 | 610.5 | 632.8 | 650.8 | 663.1 | 433.1 | 121.1 | 120.8 | 190.5 | 467 | 532.2 | 722.5 | 762 | 767 | 804.3 | 820.4 | 780.4 | 739.3 | 680.3 | 679.7 | 420.5 | 345.8 | 355.3 | 509.3 | 723.3 | 639.6 | 681 | 597.1
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1690MW at 8:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1181 | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1262.29 | 1368.49 | 1522.99 | 1558.99 | 1666.49 | 1689.99 | 1538.19 | 1572.69 | 1638.09 | 1545.99 | 1462.99 | 1514.19 | 1528.99 | 1484.89 | 1543.79 | 1551.89 | 1642.39 | 1691.79 | 1805.59 | 1693.99 | 1624.69 | 1581.99 | 1490.09 | 1326.39 | 1280.39
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1689.99 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1689.99 MW
Solu Khola Dudhkoshi(86) | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 86 | 25.4 | 25.4
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 28
Super Dordi (54) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 54 | 9.9 | 9.9 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/28)
Likhu-IV(52.4) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 52.4 | 13.5 | 13.5
Upper Marsyangdi "A"(50) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 25 | 25 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 45 | 16.9 | 16.9 |  | IPP | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 53.2 | 218.2 | 438.2 | 268.2 | 138.2 | 148.2
Mistri Khola(42) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 42 | 6.5 | 6.5 |  | NEA ROR PROR | 110.44 | 110.44 | 110.44 | 76.44 | 102.24 | 90.84 | 198.34 | 291.54 | 364.84 | 313.34 | 221.34 | 241.54
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 38.46 | 11.8 | 11.8 |  | IMPORT | 597.1 | 581.55 | 579.18 | 600.17 | 593.2 | 610.5 | 650.8 | 433.1 | 120.8 | 190.5 | 467 | 532.2
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 300 | 280 | 250
Nyadi(30) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 30 | 7.6 | 7.6 |  | System_Load | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1368.49 | 1558.99 | 1689.99 | 1538.19 | 1572.69 | 1638.09
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 28 | 6.3 | 6.3 |  | National_Load | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1368.49 | 1558.99 | 1689.99 | 1538.19 | 1572.69 | 1638.09
Dordi(27) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 30 | 9.3 | 9.3
Upper Madi(25) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 25 | 8.7 | 8.7
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 25 | 6.4 | 6.4
Solu Khola(23.5) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 23.5 | 6.5 | 6.5
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 22 | 6.1 | 6.1
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 7.5 | 7.5
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 18.4 | 18.4 | 18.4 | 21.5 | 21.5 | 20.2 | 19.1 | 18.8 | 19.4 | 19.1 | 18.1 | 18 | 18 | 18 | 18.8 | 18.8 | 18.8 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 15.5 | 17.12 | 17.12 | 17.12 | 17.12 | 240 | 21.6 | 15.5
Total IPP | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 1042.4 | 466.15 | 466.15
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 180 | 380 | 400 | 230 | 100 | 110 | 80 | 40 | 70 | 66 | 0 | 0 | 0 | 50 | 100 | 304 | 300 | 190 | 50 | 0 | 20 | 0 | 456 | 400 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 20 | 14 | 14 | 14 | 22.1 | 20 | 0
Total NEA SUBSIDIARIES | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 38.2 | 53.2 | 114.2 | 218.2 | 418.2 | 438.2 | 268.2 | 138.2 | 148.2 | 118.2 | 67 | 97 | 93 | 27 | 27 | 27 | 77 | 127 | 335.3 | 327 | 217 | 97 | 41 | 61 | 41 | 538.1 | 438.2 | 27
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 31.9 | 62 | 93.2 | 92.5 | 144.2 | 143.5 | 110 | 60 | 71.2 | 61 | 40 | 47 | 47 | 47 | 48.9 | 49 | 49 | 49 | 136.9 | 141.3 | 139.5 | 112 | 30.5 | 30.5 | 0 | 144 | 144.2 | 0
Middle MRS(70) | 34.8 | 34.8 | 34.8 | 0 | 0 | 0 | 0 | 23.9 | 31.1 | 46.8 | 46.1 | 52.7 | 53 | 25 | 24.6 | 25 | 25 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 45.7 | 27 | 34.4 | 34.4 | 24.8 | 24.8 | 0 | 70 | 53 | 0
MRS(69) | 0 | 0 | 0 | 0.8 | 23.1 | 0 | 0 | 19.2 | 64.1 | 51.1 | 69.6 | 60 | 55 | 42 | 42.6 | 46 | 23 | 23 | 23 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 47.5 | 47.5 | 45.7 | 45.7 | 32.9 | 32.9 | 14 | 69 | 69.6 | 0
U Trisuli 3A(60) | 34.5 | 34.5 | 34.5 | 34.5 | 38 | 39.3 | 37.1 | 37.1 | 35 | 36.3 | 36.3 | 36.3 | 36 | 36 | 37 | 37 | 35 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 32 | 30 | 30 | 30 | 36.3 | 60 | 39.3 | 30
CHM(30) | 0 | 0 | 0 | 0 | 0 | 10.4 | 15 | 15 | 15 | 23 | 23 | 28 | 15 | 14 | 10 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8 | 14 | 14.6 | 14.6 | 9.7 | 9.7 | 10.2 | 30 | 28 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 3.2 | 3.2 | 3.2 | 15 | 15 | 15 | 14.3 | 9.8 | 4.4 | 1.4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | [14 empty] | Tanakpur | 46 | 44 | 52.9 | 54 | 38 | 51.7 | 44 | 52.8 | 65.3 | 55 | 53.2 | 71.5 | 71 | 66 | 54.7 | 56 | 57 | 59.4 | 58.3 | 68.3 | 71.8 | 58 | 55 | 50.4
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 15 | 15 | 15 | 15 | 24 | 15 | 0 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 5 | [14 empty] | Muz | 362 | 377.8 | 385.31 | 430 | 430 | 436.6 | 240 | 0 | 53.2 | 339 | 407 | 475 | 473 | 489 | 508.2 | 539 | 512.6 | 432.3 | 200.9 | 100 | 419 | 361 | 385 | 394.6
DEVI(14.1) | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 14.1 | 11.4 | 0 | [14 empty] | Ram | 4 | 4.4 | 5 | 5.2 | 4.9 | 6.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 46 | 43.7 | 52 | 47.4 | 38.4 | 25 | 22.3 | 20.4 | 47.5 | 43.6 | 53 | 3.9
MODI(14) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.9 | 2 | 2 | 2 | 2 | 2 | 14 | 2 | 0 | [14 empty] | Rax | 121 | 102.4 | 104.8 | 104 | 106.2 | 105 | 67 | 0 | 0 | 0 | 0 | 102 | 100 | 96.1 | 117.2 | 106 | 100.4 | 91.6 | 65 | 92.6 | 111 | 103 | 118 | 101.2
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 49 | 50.58 | 52.16 | 0 | 31.4 | 51 | 73.8 | 68 | 72 | 73 | 72 | 74 | 72 | 72.2 | 72.2 | 72 | 72 | 72 | 74 | 74 | 74 | 74 | 70 | 47
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 46 | 44 | 52.9 | 54 | 38 | 51.7 | 44 | 52.8 | 65.3 | 55 | 53.2 | 71.5 | 71 | 66 | 54.7 | 56 | 57 | 59.4 | 58.3 | 68.3 | 71.8 | 58 | 55 | 50.4
Total ROR | 110.44 | 110.44 | 110.44 | 76.44 | 102.24 | 90.84 | 125.14 | 198.34 | 279.54 | 291.54 | 361.04 | 364.84 | 313.34 | 221.34 | 241.54 | 239.14 | 167.84 | 184.04 | 165.54 | 171.34 | 170.24 | 169.44 | 168.94 | 168.94 | 313.94 | 282.84 | 282.94 | 268.44 | 159.64 | 159.64 | 92.24 | 489.91 | 364.84 | 76.44 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.79167: 14; 0.8125: 14; 0.83333: 30; 0.85417: 0; 0.875: 0 | 60 | 30 | 0 | [15 empty] | 362 | 377.8 | 385.31 | 430 | 430 | 436.6 | 240 | 0 | 53.2 | 339 | 407 | 475 | 473 | 489 | 508.2 | 539 | 512.6 | 432.3 | 200.9 | 100 | 419 | 361 | 385 | 394.6
KL2(32) | 0.79167: 4.2; 0.8125: 6; 0.83333: 17; 0.85417: 8.1; 0.875: 0 | 32 | 17 | 0 | [15 empty] | 4 | 4.4 | 5 | 5.2 | 4.9 | 6.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 46 | 43.7 | 52 | 47.4 | 38.4 | 25 | 22.3 | 20.4 | 47.5 | 43.6 | 53 | 3.9
KL3(14) | 0.79167: 1.5; 0.8125: 2.2; 0.83333: 6.3; 0.85417: 3; 0.875: 0 | 14 | 6.3 | 0 | [15 empty] | 121 | 102.4 | 104.8 | 104 | 106.2 | 105 | 67 | 0 | 0 | 0 | 0 | 102 | 100 | 96.1 | 117.2 | 106 | 100.4 | 91.6 | 65 | 92.6 | 111 | 103 | 118 | 101.2
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7 | 22.2 | 53.3 | 11.1 | 0 | 0 | 0 | 106 | 53.3 | 0 | [15 empty] | 49 | 50.58 | 52.16 | 0 | 31.4 | 51 | 73.8 | 68 | 72 | 73 | 72 | 74 | 72 | 72.2 | 72.2 | 72 | 72 | 72 | 74 | 74 | 74 | 74 | 70 | 47
TANAKPUR | 50.4 | 46.2 | 44 | 52.9 | 54 | 38 | 45 | 51.7 | 52.3 | 44 | 53.9 | 52.8 | 65.3 | 55 | 53.2 | 71.5 | 71 | 66 | 54.7 | 56 | 57 | 55.3 | 59.4 | 62.6 | 58.3 | 63.1 | 68.3 | 63.3 | 71.8 | 58 | 55 |  | 71.8 | 38
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 394.6 | 361.6 | 377.8 | 385.31 | 430 | 430 | 448.3 | 436.6 | 410 | 240 | 0 | 0 | 53.2 | 339 | 407 | 475 | 473 | 489 | 508.2 | 539 | 512.6 | 480.5 | 432.3 | 462.5 | 200.9 | 94.6 | 100 | 250 | 419 | 361 | 385 |  | 539 | 0
RAMNAGAR | 3.9 | 3.9 | 4.4 | 5 | 5.2 | 4.9 | 5.5 | 6.5 | 8.3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 43.7 | 52 | 47.4 | 38.4 | 22.7 | 25 | 23.4 | 22.3 | 21.1 | 20.4 | 35 | 47.5 | 43.6 | 53 |  | 53 | 0 | [22 empty] | 46 | 0 | 362 | 4 | 121 | 49
RAXAUL 132 | 101.2 | 120.6 | 102.4 | 104.8 | 104 | 106.2 | 84 | 105 | 112.5 | 67 | 0 | 0 | 0 | 0 | 0 | 102 | 100 | 96.1 | 117.2 | 106 | 100.4 | 108.8 | 91.6 | 57.2 | 65 | 93 | 92.6 | 87 | 111 | 103 | 118 |  | 120.6 | 0 | [22 empty] | 44 | 0 | 377.8 | 4.4 | 102.4 | 50.58
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 52.9 | 0 | 385.31 | 5 | 104.8 | 52.16
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 54 | 0 | 430 | 5.2 | 104 | 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 38 | 0 | 430 | 4.9 | 106.2 | 31.4
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 51.7 | 0 | 436.6 | 6.5 | 105 | 51
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 44 | 0 | 240 | 8.3 | 67 | 73.8
SAMPATIYA 132 kV | 47 | 49.25 | 50.58 | 52.16 | 0 | 31.4 | 50 | 51 | 80 | 73.8 | 67.2 | 68 | 72 | 73 | 72 | 74 | 72 | 72.2 | 72.2 | 72 | 72 | 72 | 72 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 70 |  | 80 | 0 | [22 empty] | 52.8 | 0 | 0 | 0 | 0 | 68
Total IMPORT | 597.1 | 581.55 | 579.18 | 600.17 | 593.2 | 610.5 | 632.8 | 650.8 | 663.1 | 433.1 | 121.1 | 120.8 | 190.5 | 467 | 532.2 | 722.5 | 762 | 767 | 804.3 | 820.4 | 780.4 | 739.3 | 680.3 | 679.7 | 420.5 | 345.8 | 355.3 | 509.3 | 723.3 | 639.6 | 681 | 0 | 820.4 | 120.8 | [22 empty] | 65.3 | 0 | 53.2 | 0 | 0 | 72
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 55 | 0 | 339 | 0 | 0 | 73
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 53.2 | 0 | 407 | 0 | 0 | 72
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 71.5 | 0 | 475 | 0 | 102 | 74
Total THERMAL | [31 empty] | 55.4 | 0 | 0 | [22 empty] | 71 | 0 | 473 | 46 | 100 | 72
TOTAL SYSTEM LOAD (ACTUAL) | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1262.29 | 1368.49 | 1522.99 | 1408.99 | 1366.49 | 1389.99 | 1238.19 | 1292.69 | 1388.09 | 1545.99 | 1462.99 | 1514.19 | 1528.99 | 1484.89 | 1443.79 | 1401.89 | 1392.39 | 1441.79 | 1555.59 | 1443.99 | 1374.69 | 1351.99 | 1390.09 | 1326.39 | 1280.39 | 2231.81 | 1555.59 | 1180.96 | [22 empty] | 66 | 0 | 489 | 43.7 | 96.1 | 72.2
Interruption/Tripping | 0: 0; 0.041667: 0; 0.083333: 0; 0.29167: 150; 0.3125: 300; 0.33333: 300; 0.375: 300; 0.41667: 280; 0.45833: 250; 0.70833: 100; 0.72917: 150; 0.75: 250; 0.77083: 250; 0.79167: 250; 0.8125: 250; 0.83333: 250; 0.85417: 230; 0.875: 100 |  | 300 | 0 | [22 empty] | 54.7 | 0 | 508.2 | 52 | 117.2 | 72.2
TOTAL SYSTEM LOAD (EXPECTED) | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1262.29 | 1368.49 | 1522.99 | 1558.99 | 1666.49 | 1689.99 | 1538.19 | 1572.69 | 1638.09 | 1545.99 | 1462.99 | 1514.19 | 1528.99 | 1484.89 | 1543.79 | 1551.89 | 1642.39 | 1691.79 | 1805.59 | 1693.99 | 1624.69 | 1581.99 | 1490.09 | 1326.39 | 1280.39 | 1693.71 | 1805.59 | 1180.96 | [22 empty] | 56 | 0 | 539 | 47.4 | 106 | 72
TOTAL NATIONAL LOAD (ACTUAL) | 1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1262.29 | 1368.49 | 1522.99 | 1558.99 | 1666.49 | 1689.99 | 1538.19 | 1572.69 | 1638.09 | 1545.99 | 1462.99 | 1514.19 | 1528.99 | 1484.89 | 1543.79 | 1551.89 | 1642.39 | 1691.79 | 1805.59 | 1693.99 | 1624.69 | 1581.99 | 1490.09 | 1326.39 | 1280.39 |  | 1805.59 | 1180.96 | [22 empty] | 57 | 0 | 512.6 | 38.4 | 100.4 | 72
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 59.4 | 0 | 432.3 | 25 | 91.6 | 72
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58.3 | 0 | 200.9 | 22.3 | 65 | 74
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 68.3 | 0 | 100 | 20.4 | 92.6 | 74
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 71.8 | 0 | 419 | 47.5 | 111 | 74
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58 | 0 | 361 | 43.6 | 103 | 74
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 55 | 0 | 385 | 53 | 118 | 70
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 50.4 | 0 | 394.6 | 3.9 | 101.2 | 47
NET IMPORT | 597.1 | 581.55 | 579.18 | 600.17 | 593.2 | 610.5 | 632.8 | 650.8 | 663.1 | 433.1 | 121.1 | 120.8 | 190.5 | 467 | 532.2 | 722.5 | 762 | 767 | 804.3 | 820.4 | 780.4 | 739.3 | 680.3 | 679.7 | 420.5 | 345.8 | 355.3 | 509.3 | 723.3 | 639.6 | 681 |  | 820.4 | 120.8
HZ | 50.02 | 50.03 | 49.97 | 49.93 | 50.001 | 50.021 | 49.991 | 49.996 | 49.996 | 49.996 | 50.038 | 50.028 | 50.079 | 49.865 | 49.99 | 49.985 | 49.99 | 50.48 | 50.03 | 49.86 | 50.05 | 50.07 | 50.09 | 49.99 | 49.9 | 49.8 | 50.7 | 49.91 | 50.057 | 50.027 | 49.931 |  | 50.7 | 49.8
HTD 132KV | 128.2 | 129.1 | 129.1 | 129.4 | 126.8 | 129 | 127.6 | 126.8 | 126.8 | 126.8 | 125.4 | 126 | 126.6 | 126.4 | 124.6 | 122.5 | 124 | 121.2 | 121.8 | 121.7 | 125.5 | 125.5 | 127.5 | 125.6 | 129 | 129 | 131 | 131.2 | 130.3 | 131.2 | 129.8 |  | 131.2 | 121.2
SUI 132KV | 132.5 | 133.3 | 133.3 | 132.9 | 131.4 | 133 | 131.5 | 130.7 | 130.7 | 130.7 | 127.5 | 128 | 129.3 | 129.2 | 127.8 | 126.1 | 127.9 | 126 | 126 | 126.3 | 129.4 | 129.4 | 131.1 | 127 | 129.7 | 129.7 | 132 | 132.6 | 132.6 | 134 | 134.2 |  | 134.2 | 126
DUBI 132KV | 129.2 | 127.5 | 127.5 | 129.2 | 130.9 | 130.6 | 129 | 122 | 122 | 122 | 124.1 | 126.8 | 129 | 127.4 | 126.6 | 123.7 | 124.5 | 119.9 | 119.9 | 125.9 | 126 | 126 | 127.2 | 127.4 | 128.7 | 128.7 | 133 | 131.5 | 130.2 | 126.7 | 129 |  | 133 | 119.9
ANAMANI 132KV | 131.7 | 130.8 | 130.8 | 132.8 | 134.5 | 131.9 | 132.1 | 129.7 | 129.7 | 129.7 | 122.1 | 126 | 127.1 | 125.4 | 125 | 122.5 | 124.1 | 131.5 | 131.5 | 123.6 | 124.8 | 124.8 | 125.3 | 124.8 | 126.5 | 126.5 | 132.6 | 131.9 | 131.1 | 128.9 | 132 |  | 134.5 | 122.1
KG-A 132KV | 131.5 | 131.4 | 131.4 | 131.7 | 129.6 | 134 | 134.2 | 135.5 | 135.5 | 135.5 | 134.5 | 122.7 | 135.1 | 136.2 | 132 | 133 | 135.3 | 129.4 | 129.4 | 132 | 136.3 | 136.3 | 136.5 | 133.7 | 135.4 | 135.4 | 135 | 135.3 | 136.4 | 135.6 | 135.6 |  | 136.5 | 122.7
KOHALPUR 132KV | 130 | 133 | 133 | 131.8 | 130.3 | 132.1 | 129.1 | 129.7 | 129.7 | 129.7 | 131.7 | 131 | 127.7 | 128.2 | 131.7 | 128.5 | 130.2 | 134.4 | 134.4 | 131.9 | 135.7 | 135.7 | 132.4 | 132.7 | 132.6 | 132.6 | 132 | 131.4 | 131.8 | 133 | 131.6 |  | 135.7 | 127.7
SUI 66KV | 66.6 | 67 | 67 | 66.8 | 66.1 | 66.9 | 66.1 | 66.2 | 66.2 | 66.2 | 63.6 | 64.6 | 64.9 | 64.7 | 64 | 63.5 | 64.2 | 63.2 | 63.2 | 63.4 | 65.1 | 65.1 | 65.8 | 63.8 | 64.4 | 64.4 | 66.3 | 66.4 | 66.5 | 67.4 | 67.5 |  | 67.5 | 63.2
[33 empty] | 0 | 0
Kathmandu Load | 159.52 | 128.16 | 124.24 | 120.558 | 129.033 | 153.609 | 179.782 | 220.13 | 218.03 | 304.69 | 325.94 | 333.64 | 317.04 | 309.44 | 42 | 311.26 | 276.42 | 281.884 | 285.94 | 288.66 | 297.76 | 304.22 | 325.3 | 385.84 | 390 | 361.3 | 309.74 | 293.34 | 255.24 | 184.14 | 145.84 |  | 390 | 42
MRS-SYU | -4.2 | -4.5 | -8.9 | -15.7 | -22.1 | -16.1 | -11 | 9.3 | 9.3 | 28.5 | 49.4 | 49 | 45.2 | 29.1 | 26.3 | 20.8 | 20.2 | 17.3 | 19.2 | 21.1 | 25.6 | 27.6 | 27.6 | 29.7 | 39.54 | 43.9 | 50.7 | 40 | 25.9 | 17 | 2 | 75 | 50.7 | -22.1
NMRS-MATA | -7.9 | -8.8 | -13.4 | -24.5 | -33.8 | -26.1 | -19.5 | 8 | 8 | 40.5 | 68.4 | 68.4 | 64.3 | 41.4 | 37 | 22.2 | 21.5 | 21.4 | 20.6 | 23.3 | 29.8 | 31.3 | 33.6 | 38.3 | 51.1 | 55.9 | 64.6 | 51 | 28.4 | 16.5 | -2 | 240 | 68.4 | -33.8
KL2-MATA | -15 | -18 | -19 | -14.6 | -11.5 | -4 | 1.9 | 4.5 | 4.5 | 22.3 | 3.8 | 7.8 | 3 | 17 | 0 | 18 | 19 | 18 | 25 | 32 | 39 | 41.7 | 49 | 73 | 58 | 51 | 24.6 | 35 | 25 | -4 | -12 | 240 | 73 | -19
KL1-SYU | 8.9 | -8.5 | -10.9 | -8.6 | -11.4 | -1.5 | -2.3 | 4.6 | 4.6 | 16.5 | 15.6 | 15 | 13 | 14 | 0 | 0 | 2.6 | 0 | 0.2 | 1.2 | 9.7 | 7.5 | 22.2 | 24.1 | 30.3 | 31.2 | 39.3 | 18 | 9 | 0.5 | -1 | 60 | 39.3 | -11.4
KHIMTI-LAMOSANGHU | 89.28 | 79.52 | 88 | 95.518 | 115.893 | 108.069 | 119.642 | 102.69 | 102.69 | 105.95 | 97.8 | 100 | 98.4 | 114.8 | 125 | 144.32 | 134.48 | 146.944 | 147.2 | 142.72 | 128.32 | 131.68 | 128.96 | 156.8 | 141.12 | 115.36 | 71 | 76.8 | 94.4 | 81.6 | 80 | 120 | 156.8 | 71
LAMOSHANGU-BHAKTAPUR | 67.9 | 63.9 | 67.1 | 71.2 | 81.7 | 77.3 | 83 | 73.9 | 73.9 | 75.3 | 70 | 73.8 | 68 | 80 | 86.8 | 93.9 | 89 | 92.3 | 94.4 | 92.4 | 85.7 | 87 | 87.6 | -23.5 | 91.5 | 78.3 | 59.6 | 62 | 69 | 65.1 | 64
BALAJU-SYUCHATAR | 54.5 | 50.5 | 58.6 | 65.9 | 75.9 | 57 | 60.2 | 27.2 | 27.2 | -16.3 | -34.9 | -32.9 | -30 | -8 | 12.7 | 24.4 | 20 | 23.1 | 26.2 | 16.5 | 2.3 | -3.4 | -9.6 | -24.8 | -32.5 | -41.4 | -60.9 | -35 | 1 | 22.3 | 40
DHALKE-NAWALPUR I | 72.2 | 64 | 70.3 | 76 | 90.2 | 85.5 | 90.4 | 78.2 | 78.2 | 64 | 50.1 | 56.3 | 51 | 81 | 97 | 97.5 | 95 | 94 | 97.3 | 99.5 | 89.4 | 89.8 | 86.6 | 87 | 72.4 | 52.8 | 28.8 | 50 | 65 | 62 | 65 |  | 99.5 | 28.8
N. BHARATPUR-BARDGHAT I | 20.1 | 14.6 | 25.1 | 22.7 | 27.3 | 17 | 12.4 | 2.6 | 2.6 | 0 | -19.2 | -21.7 | -17 | -7.5 | -9.6 | 1.2 | -6.5 | -3.7 | -4.8 | -3.9 | -5.6 | -7.1 | -3.7 | -14.2 | -23.3 | -25.9 | -29.2 | -17 | -3 | 3.3 | 7 |  | 27.3 | -29.2
DAMAK-DUHABI | -13.8 | -12.5 | -11.5 | -11.1 | -12.2 | -17.1 | -22 | -32.9 | -32.9 | -48.1 | -50.4 | -54.8 | -41 | -45 | -37.8 | -37 | -33 | -32.9 | -36.6 | -46 | -44.4 | -47.8 | -54 | -65.2 | -59.7 | -50.6 | -41.4 | -39 | -34 | -22 | -17.3 |  | -11.1 | -65.2
HETAUDA-KAMANE | -16.4 | -10.8 | -16.7 | -17.8 | 33.2 | -23.6 | -30.2 | -15.7 | -15.7 | -14.5 | 16.1 | 12.4 | 13 | -9 | -14 | -27 | -24 | -25.7 | -29.9 | -36.8 | -39.5 | -44.8 | -40.5 | -48 | -33.7 | -19.2 | -1.2 | -12 | -24.1 | -7.3 | -7 |  | 33.2 | -48
MIRCHAIYA LAHAN 2 | 95.3 | 100.8 | 98.7 | 95.9 | 88.2 | 95.4 | 100.8 | 109.5 | 109.5 | 114 | 106.5 | 109.7 | 100.5 | 99 | 128 | 122 | 123 | 127 | 126.7 | 120.2 | 116.3 | 110.5 | 102.3 | 124.9 | 110.9 | 99.2 | 98.1 | 97 | 109 | 114 | 102.3 |  | 128 | 88.2
Water Level
UTK | 1984.48 | 1984.7 | 1984.9 | 1985.12 | 1985.31 | 1985.5 |  | 1985.72 |  | 1985.72 |  | 1985.1 | 1984.15 | 1983.63 | 1983.55 | 1983.5 | 1983.58 | 1983.65 | 1983.69 | 1983.8 | 1984.02 |  | 1984.21 |  | 1983.8 |  | 1983.38 |  | 1983.1 | 1983.31 | 1983.55
KGA | 520.75 | 521.12 | 521.42 | 521.72 | 522 | 522.3 |  | 522.36 |  | 522.14 |  | 521.64 | 521 | 520.376 | 520.69 | 520.58 | 520.57 | 520.69 | 520.73 | 520.8 | 520.83 |  | 520.88 |  | 520.68 |  | 519.99 |  | 519.67 | 519.86 | 520.2
MMRS | 622.31 | 622.22 | 522.16 | 622.25 | 622.71 | 623.12 |  | 623.3 |  | 623.14 |  | 622.82 | 622.27 | 622.3 | 622.34 | 622.4 | 622.46 | 622.6 | 622.47 | 622.37 | 622.29 |  | 622.21 |  | 622.01 |  | 621.75 |  | 621.77 | 621.86 | 622.21
MRS | 335.13 | 335.43 | 335.78 | 336.1 | 336.21 | 336.28 |  | 336.54 |  | 336.54 |  | 336.22 | 335.92 | 335.67 | 335.46 | 335.17 | 334.88 | 335.18 | 335.45 | 335.62 | 335.61 |  | 335.56 |  | 335.44 |  | 335.33 |  | 335.23 | 335.25 | 335.26
CHM | 884.2 | 884.9 | 885.5 | 886.1 | 886.7 | 887 |  | 886.8 |  | 886.4 |  | 885.5 | 884.1 | 883.5 | 883.5 | 883.2 | 882.8 | 882.6 | 882.9 | 883.5 | 884.4 |  | 885.06 |  | 885.4 |  | 884.6 |  | 884.2 | 884.2 | 884.1
KL 1 | 0: 1519.74; 0.45833: 1519.75; 0.91667: 1519.75
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1689.99; 0.041667: 8:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/28)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 29
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/29 |  |  | 2080/10/29 |  |  | Tuesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 658.7 | 638 | 599.7 | 619.1 | 612.6 | 627.4 | 631 | 620.3 | 537.1 | 120.8 | 122.8 | 277.8 | 526.9 | 629.5 | 698.6 | 672 | 820.4 | 816.9 | 872.8 | 755.2 | 743.3 | 627.1 | 815.8 | 525.4 | 348.3 | 395.5 | 392 | 602 | 621.7 | 654 | 637
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1784MW at 9:00hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1186 | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1262.19 | 1364.59 | 1499.59 | 1527.09 | 1649.29 | 1646.19 | 1783.99 | 1546.59 | 1650.59 | 1495.99 | 1436.49 | 1522.59 | 1530.89 | 1567.49 | 1559.49 | 1578.99 | 1538.49 | 1823.29 | 2025.39 | 1971.69 | 1682.99 | 1560.89 | 1414.29 | 1353.99 | 1259.29
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1783.99 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1783.99 MW
Solu Khola Dudhkoshi(86) | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.5 | 25.5 | 25.5 | 25.5 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 86 | 25.5 | 24.4
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 29
Super Dordi (54) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 54 | 10.1 | 9.8 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/29)
Likhu-IV(52.4) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 12.3 | 12.3 | 12.3 | 12.3 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 52.4 | 13.5 | 11.2
Upper Marsyangdi "A"(50) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 50 | 25.3 | 25 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 15.2 | 15.2 | 15.2 | 15.2 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 15 | 15 | 15 | 15 | 15 | 45 | 16.9 | 13.8 |  | IPP | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 463.45 | 463.45 | 463.45 | 463.45
Super Madi ( 44 ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 44 | 16 |  | NEA SUB | 41 | 41 | 41 | 42 | 42 | 38.2 | 53.2 | 198.1 | 473.2 | 473.2 | 58.2 | 58.2
Mistri Khola(42) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 42 | 7 | 6.5 |  | NEA ROR PROR | 78.04 | 78.04 | 78.04 | 78.04 | 78.04 | 106.04 | 214.24 | 275.74 | 336.74 | 319.54 | 248.04 | 249.44
Upper Chameliya(40) | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 38.46 | 11.8 | 11 |  | IMPORT | 637 | 658.7 | 638 | 599.7 | 619.1 | 612.6 | 631 | 537.1 | 122.8 | 277.8 | 526.9 | 629.5
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 250 | 250 | 250 | 250
Nyadi(30) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 30 | 7.6 | 7.6 |  | System_Load | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1364.59 | 1527.09 | 1646.19 | 1783.99 | 1546.59 | 1650.59
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 28 | 6.3 | 6.3 |  | National_Load | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1364.59 | 1527.09 | 1646.19 | 1783.99 | 1546.59 | 1650.59
Dordi(27) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 30 | 9.3 | 9.3
Upper Madi(25) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 25 | 8.7 | 8.7
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6
Upper Dordi (25) | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 25 | 6.6 | 6.4
Solu Khola(23.5) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 23.5 | 6.5 | 6.5
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 22 | 6.1 | 6.1
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8
Dordi12) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 7.5 | 7.5
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 20.5 | 20.5 | 18.5 | 20.3 | 20.3 | 20.4 | 20.3 | 17 | 15.5 | 15.6 | 16.7 | 17.1 | 17.1 | 17.8 | 19.2 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 240 | 21 | 15.5
Total IPP | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 466.15 | 463.45 | 463.45 | 463.45 | 463.45 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 462.75 | 461.25 | 461.25 | 461.25 | 461.25 | 461.25 | 1042.4 | 466.15 | 461.25
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 110 | 160 | 456 | 435 | 435 | 20 | 20 | 60 | 20 | 20 | 30 | 0 | 0 | 0 | 0 | 0 | 228 | 300 | 180 | 160 | 40 | 0 | 0 | 456 | 456 | 0
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27
Chilime(22.1) | 14 | 14 | 14 | 15 | 15 | 11.2 | 11.2 | 11.2 | 11.2 | 11.1 | 11 | 11.2 | 11.2 | 11.2 | 11.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 22.1 | 15 | 9.2
Total NEA SUBSIDIARIES | 41 | 41 | 41 | 42 | 42 | 38.2 | 38.2 | 53.2 | 148.2 | 198.1 | 494 | 473.2 | 473.2 | 58.2 | 58.2 | 96.3 | 56.3 | 56.3 | 66.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 264.3 | 336.3 | 216.2 | 196.2 | 76.2 | 36.2 | 36.2 | 538.1 | 494 | 36.2
KGA(144) | 0 | 0 | 0 | 0 | 0 | 28 | 40.7 | 73 | 81.2 | 91.3 | 113.8 | 116.1 | 116.1 | 70 | 61.8 | 61.7 | 60.1 | 31 | 31 | 45.2 | 45.2 | 30.8 | 62.2 | 97.8 | 142.8 | 142.8 | 141.4 | 141.4 | 121 | 81 | 0 | 144 | 142.8 | 0
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 29.9 | 54.4 | 58.5 | 54.9 | 46 | 44 | 45.9 | 43 | 24.8 | 24.8 | 24.8 | 25.1 | 24.9 | 24.9 | 34.8 | 34.8 | 67.6 | 65.2 | 65.2 | 30 | 30 | 0 | 70 | 67.6 | 0
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.9 | 46 | 46.2 | 46.2 | 63.2 | 50.9 | 34 | 33 | 34.4 | 46 | 23.6 | 23.6 | 23.6 | 23.6 | 16.4 | 16.5 | 67 | 69.3 | 69.3 | 68.9 | 68.9 | 51 | 51 | 35 | 69 | 69.3 | 0
U Trisuli 3A(60) | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 38 | 38.3 | 37.3 | 37.3 | 36.5 | 36.8 | 36.8 | 34.3 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 60 | 38.3 | 31.3
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.3 | 28.7 | 28.6 | 22.9 | 14.8 | 10 | 9.4 | 15 | 0 | 0 | 9.5 | 14.6 | 14.6 | 14.6 | 10.5 | 14.8 | 14.8 | 28 | 28 | 14.1 | 14.1 | 0 | 0 | 0 | 30 | 28.7 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 2.8 | 5.6 | 9.1 | 12.6 | 17.4 | 17.5 | 17.5 | 15.4 | 12.1 | 8.6 | 1.5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17.5 | 0 | [14 empty] | Tanakpur | 54 | 58 | 62 | 49 | 43 | 72 | 59.5 | 54.3 | 58.8 | 53.9 | 52.3 | 52.6 | 53 | 63.9 | 69.9 | 71.7 | 67 | 65.6 | 69 | 69.1 | 68 | 60.7 | 55 | 41
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 24 | 15 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 5 | [14 empty] | Muz | 397 | 386 | 376 | 403.8 | 440 | 454 | 345 | 6.2 | 155 | 408 | 412 | 460 | 427 | 515.8 | 507.8 | 567.7 | 477.5 | 338.9 | 237.8 | 123 | 308 | 355 | 388 | 374
DEVI(14.1) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 9 | 9 | 9 | 9 | 9 | 14.1 | 10.6 | 9 | [14 empty] | Ram | 36 | 33 | 5.7 | 5.3 | 5.6 | 7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7 | 40.2 | 43.4 | 37.7 | 41.2 | 43.1 | 37.8 | 40 | 36 | 39 | 32
MODI(14) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 14 | 2.8 | 2 | [14 empty] | Rax | 120 | 111 | 106 | 111 | 124 | 98 | 75 | 0 | 0 | 0 | 97.2 | 108 | 120 | 120 | 114 | 107 | 106 | 106.4 | 104.5 | 103.6 | 124 | 108 | 110 | 120
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10.05 | 4.5 | 4.5 | [14 empty] | Sam | 52 | 50 | 50 | 50 | 0 | 0 | 49 | 62.3 | 64 | 65 | 68 | 78 | 72 | 79 | 85 | 83 | 67 | 75 | 71 | 62 | 62 | 62 | 62 | 70
PUWA(6.2) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 6.2 | 1.7 | 1.7
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 54 | 58 | 62 | 49 | 43 | 72 | 59.5 | 54.3 | 58.8 | 53.9 | 52.3 | 52.6 | 53 | 63.9 | 69.9 | 71.7 | 67 | 65.6 | 69 | 69.1 | 68 | 60.7 | 55 | 41
Total ROR | 78.04 | 78.04 | 78.04 | 78.04 | 78.04 | 106.04 | 130.44 | 214.24 | 264.94 | 275.74 | 318.34 | 336.74 | 319.54 | 248.04 | 249.44 | 238.34 | 245.44 | 183.14 | 184.94 | 195.64 | 188.84 | 162.04 | 197.24 | 293.24 | 353.74 | 386.54 | 362.44 | 362.44 | 274.84 | 234.84 | 107.84 | 489.91 | 386.54 | 78.04 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | 0.70833: 10; 0.72917: 14; 0.75: 10; 0.77083: 10; 0.79167: 14; 0.8125: 30; 0.83333: 30; 0.85417: 0; 0.875: 0; 0.91667: 0; 0.95833: 0 | 60 | 30 | 0 | [15 empty] | 397 | 386 | 376 | 403.8 | 440 | 454 | 345 | 6.2 | 155 | 408 | 412 | 460 | 427 | 515.8 | 507.8 | 567.7 | 477.5 | 338.9 | 237.8 | 123 | 308 | 355 | 388 | 374
KL2(32) | 0.70833: 4.7; 0.72917: 8.1; 0.75: 3.7; 0.77083: 3.8; 0.79167: 3.8; 0.8125: 5.7; 0.83333: 12.9; 0.85417: 7; 0.875: 0; 0.91667: 0; 0.95833: 0 | 32 | 12.9 | 0 | [15 empty] | 36 | 33 | 5.7 | 5.3 | 5.6 | 7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7 | 40.2 | 43.4 | 37.7 | 41.2 | 43.1 | 37.8 | 40 | 36 | 39 | 32
KL3(14) | 0.70833: 1.7; 0.72917: 2.5; 0.75: 1.4; 0.77083: 1.4; 0.79167: 1.4; 0.8125: 2.1; 0.83333: 4.7; 0.85417: 2; 0.875: 0; 0.91667: 0; 0.95833: 0 | 14 | 4.7 | 0 | [15 empty] | 120 | 111 | 106 | 111 | 124 | 98 | 75 | 0 | 0 | 0 | 97.2 | 108 | 120 | 120 | 114 | 107 | 106 | 106.4 | 104.5 | 103.6 | 124 | 108 | 110 | 120
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 24.6 | 15.1 | 15.2 | 19.2 | 37.8 | 47.6 | 9 | 0 | 0 | 0 | 106 | 47.6 | 0 | [15 empty] | 52 | 50 | 50 | 50 | 0 | 0 | 49 | 62.3 | 64 | 65 | 68 | 78 | 72 | 79 | 85 | 83 | 67 | 75 | 71 | 62 | 62 | 62 | 62 | 70
TANAKPUR | 41 | 54.1 | 58 | 62 | 49 | 43 | 49.5 | 72 | 66 | 59.5 | 55 | 54.3 | 58.8 | 53.9 | 52.3 | 52.6 | 53 | 63.9 | 69.9 | 71.7 | 67 | 65.4 | 65.6 | 68.9 | 69 | 64.9 | 69.1 | 67 | 68 | 60.7 | 55 |  | 72 | 41
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | 374 | 397 | 386 | 376 | 403.8 | 440 | 452 | 454 | 408 | 345 | 10.8 | 6.2 | 155 | 408 | 412 | 460 | 427 | 515.8 | 507.8 | 567.7 | 477.5 | 465 | 338.9 | 515 | 237.8 | 75.7 | 123 | 105 | 308 | 355 | 388 |  | 567.7 | 6.2
RAMNAGAR | 32 | 35.6 | 33 | 5.7 | 5.3 | 5.6 | 5.9 | 7 | 8.3 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7 | 40.2 | 43.4 | 37.7 | 37.1 | 41.2 | 44.9 | 43.1 | 42.1 | 37.8 | 41 | 40 | 36 | 39 |  | 44.9 | 0 | [22 empty] | 54 | 0 | 397 | 36 | 120 | 52
RAXAUL 132 | 120 | 120 | 111 | 106 | 111 | 124 | 120 | 98 | 89 | 75 | 0 | 0 | 0 | 0 | 97.2 | 108 | 120 | 120 | 114 | 107 | 106 | 100.8 | 106.4 | 108 | 104.5 | 108.6 | 103.6 | 117 | 124 | 108 | 110 |  | 124 | 0 | [22 empty] | 58 | 0 | 386 | 33 | 111 | 50
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 62 | 0 | 376 | 5.7 | 106 | 50
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 49 | 0 | 403.8 | 5.3 | 111 | 50
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 43 | 0 | 440 | 5.6 | 124 | 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 72 | 0 | 454 | 7 | 98 | 0
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 59.5 | 0 | 345 | 8.6 | 75 | 49
SAMPATIYA 132 kV | 70 | 52 | 50 | 50 | 50 | 0 | 0 | 0 | 49 | 49 | 55 | 62.3 | 64 | 65 | 68 | 78 | 72 | 79 | 85 | 83 | 67 | 75 | 75 | 79 | 71 | 57 | 62 | 62 | 62 | 62 | 62 |  | 85 | 0 | [22 empty] | 54.3 | 0 | 6.2 | 0 | 0 | 62.3
Total IMPORT | 637 | 658.7 | 638 | 599.7 | 619.1 | 612.6 | 627.4 | 631 | 620.3 | 537.1 | 120.8 | 122.8 | 277.8 | 526.9 | 629.5 | 698.6 | 672 | 820.4 | 816.9 | 872.8 | 755.2 | 743.3 | 627.1 | 815.8 | 525.4 | 348.3 | 395.5 | 392 | 602 | 621.7 | 654 | 0 | 872.8 | 120.8 | [22 empty] | 58.8 | 0 | 155 | 0 | 0 | 64
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 53.9 | 0 | 408 | 0 | 0 | 65
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 52.3 | 0 | 412 | 0 | 97.2 | 68
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 52.6 | 0 | 460 | 0 | 108 | 78
Total THERMAL | 0.70833: 100; 0.72917: 150; 0.75: 200; 0.77083: 200; 0.79167: 200; 0.8125: 200; 0.83333: 100; 0.85417: 70; 0.875: 0; 0.91667: 0; 0.95833: 0 | 55.4 | 200 | 0 | [22 empty] | 53 | 0 | 427 | 0 | 120 | 72
TOTAL SYSTEM LOAD (ACTUAL) | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1262.19 | 1364.59 | 1499.59 | 1477.09 | 1399.29 | 1396.19 | 1533.99 | 1296.59 | 1400.59 | 1495.99 | 1436.49 | 1522.59 | 1530.89 | 1567.49 | 1559.49 | 1578.99 | 1538.49 | 1823.29 | 1825.39 | 1771.69 | 1582.99 | 1490.89 | 1414.29 | 1353.99 | 1259.29 | 2231.81 | 1825.39 | 1185.89 | [22 empty] | 63.9 | 0 | 515.8 | 41.7 | 120 | 79
Interruption/Tripping | 0.29167: 50; 0.3125: 250; 0.33333: 250; 0.375: 250; 0.41667: 250; 0.45833: 250; 0.79167: 200; 0.8125: 200; 0.83333: 100; 0.85417: 70; 0.875: 0; 0.91667: 0; 0.95833: 0 |  | 250 | 0 | [22 empty] | 69.9 | 0 | 507.8 | 40.2 | 114 | 85
TOTAL SYSTEM LOAD (EXPECTED) | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1262.19 | 1364.59 | 1499.59 | 1527.09 | 1649.29 | 1646.19 | 1783.99 | 1546.59 | 1650.59 | 1495.99 | 1436.49 | 1522.59 | 1530.89 | 1567.49 | 1559.49 | 1578.99 | 1538.49 | 1823.29 | 2025.39 | 1971.69 | 1682.99 | 1560.89 | 1414.29 | 1353.99 | 1259.29 | 1693.71 | 2025.39 | 1185.89 | [22 empty] | 71.7 | 0 | 567.7 | 43.4 | 107 | 83
TOTAL NATIONAL LOAD (ACTUAL) | 1222.19 | 1243.89 | 1223.19 | 1185.89 | 1205.29 | 1222.99 | 1262.19 | 1364.59 | 1499.59 | 1527.09 | 1649.29 | 1646.19 | 1783.99 | 1546.59 | 1650.59 | 1495.99 | 1436.49 | 1522.59 | 1530.89 | 1567.49 | 1559.49 | 1578.99 | 1538.49 | 1823.29 | 2025.39 | 1971.69 | 1682.99 | 1560.89 | 1414.29 | 1353.99 | 1259.29 |  | 2025.39 | 1185.89 | [22 empty] | 67 | 0 | 477.5 | 37.7 | 106 | 67
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 65.6 | 0 | 338.9 | 41.2 | 106.4 | 75
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 69 | 0 | 237.8 | 43.1 | 104.5 | 71
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 69.1 | 0 | 123 | 37.8 | 103.6 | 62
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 68 | 0 | 308 | 40 | 124 | 62
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 60.7 | 0 | 355 | 36 | 108 | 62
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 55 | 0 | 388 | 39 | 110 | 62
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 41 | 0 | 374 | 32 | 120 | 70
NET IMPORT | 637 | 658.7 | 638 | 599.7 | 619.1 | 612.6 | 627.4 | 631 | 620.3 | 537.1 | 120.8 | 122.8 | 277.8 | 526.9 | 629.5 | 698.6 | 672 | 820.4 | 816.9 | 872.8 | 755.2 | 743.3 | 627.1 | 815.8 | 525.4 | 348.3 | 395.5 | 392 | 602 | 621.7 | 654 |  | 872.8 | 120.8
HZ | 50 | 49.97 | 49.96 | 49.945 | 49.902 | 50.04 | 50.012 | 50.032 | 50.088 | 50 | 50 | 50.11 | 49.958 | 49.954 | 50.027 | 50.022 | 50.057 | 49.95 | 49.84 | 49.93 | 50.03 | 50.09 | 50.07 | 50.07 | 49.84 | 49.99 | 50.051 | 50.04 | 50.07 | 50.04 | 49.85 |  | 50.11 | 49.84
HTD 132KV | 130.3 | 128 | 128.2 | 128.2 | 128.2 | 126.5 | 126.5 | 126 | 124 | 124 | 125.5 | 124.8 | 125 | 123.8 | 122.7 | 122.1 | 126.5 | 126.5 | 123.9 | 123.2 | 123.2 | 128.1 | 128.5 | 126.9 | 128.2 | 128.2 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 |  | 130.4 | 122.1
SUI 132KV | 134.7 | 132.6 | 132.7 | 132.7 | 132.7 | 130.9 | 130.9 | 129.9 | 128 | 128 | 128 | 127.3 | 127.5 | 126.8 | 126.2 | 125.8 | 129.8 | 129.8 | 127.2 | 127 | 127 | 130.7 | 130.7 | 129.1 | 128.5 | 128.5 | 132 | 132 | 132 | 133 | 133 |  | 134.7 | 125.8
DUBI 132KV | 129 | 126.6 | 130.3 | 130.3 | 130.3 | 128.6 | 128.6 | 126.8 | 123 | 123 | 123 | 124.2 | 126.1 | 124.1 | 125.1 | 127.7 | 125.7 | 125.7 | 123 | 122.6 | 122.6 | 129.3 | 129.3 | 129.3 | [8 empty] | 130.3 | 122.6
ANAMANI 132KV | 131 | 129.9 | 133 | 133 | 133 | 130 | 130 | 127.4 | 122 | 122 | 122 | 121.8 | 123.3 | 123.5 | 126 | 127.9 | 126.6 | 126.6 | 123.2 | 122.4 | 122.4 | 126.6 | 135.7 | 122.9 | 125.9 | 125.9 | 129.5 | 129.5 | 129 | 130 | 130 |  | 135.7 | 121.8
KG-A 132KV | 136 | 130 | 129 | 129 | 129 | 129.4 | 129.4 | 131.7 | 133 | 133 | 133 | 134.8 | 133.3 | 132.5 | 131.6 | 130.6 | 137 | 137 | 133.7 | 134.5 | 134.5 | 135.7 | 136.3 | 135.4 | 135.3 | 135.3 | 137.2 | 137.2 | 135 | 134.6 | 133 |  | 137.2 | 129
KOHALPUR 132KV | 135.4 | 138 | 134.3 | 134.3 | 134.3 | 134 | 134 | 132 | 133 | 133 | 133 | 131.8 | 131.3 | 129.9 | 131.1 | 133.4 | 128.6 | 128.6 | 123.7 | 122.4 | 122.4 | 130.6 | 132.3 | 130.1 | 123.3 | 123.3 | 133.4 | 133.4 | 134 | 1344 | 132 |  | 1344 | 122.4
SUI 66KV | 67.5 | 67 | 67 | 67 | 67 | 65.9 | 65.5 | 65.2 | 64.3 | 64.3 | 64 | 63.8 | 64.3 | 63.6 | 63.4 | 63 | 65.1 | 65.1 | 63.9 | 63.7 | 63.7 | 65.8 | 65.7 | 64.9 | 64.9 | 64.9 | 66.1 | 66.1 | 66.5 | 67 | 67 |  | 67.5 | 63
[33 empty] | 0 | 0
Kathmandu Load | 130.04 | 122.64 | 115.84 | 129.54 | 123.14 | 150.84 | 183.64 | 232.14 | 293.14 | 320.84 | 349.04 | 346.724 | 319.08 | 303.58 | 42 | 296.112 | 290.62 | 278.75 | 286.3 | 291.54 | 286.04 | 281.82 | 312.34 | 363.84 | 403.14 | 377.74 | 318.216 | 292.84 | 265.84 | 213.84 | 147.84 |  | 403.14 | 42
MRS-SYU | -5 | -10.1 | -12 | -6.5 | -13.5 | -19.4 | -8.8 | 0.5 | 18.1 | 23 | 38.6 | 42.6 | 45.6 | 29.8 | 16.3 | 12 | 23.7 | 12.5 | 12.9 | 16.4 | 19.5 | 12.3 | 16.9 | 35.9 | 44.8 | 54.9 | 59.3 | 49 | 44 | 34 | 6 | 75 | 59.3 | -19.4
NMRS-MATA | -13.4 | -18.1 | -20 | -13.6 | -21.6 | -30.5 | -16.7 | -6 | 19.5 | 27.3 | 56.7 | 59.7 | 65.1 | 44.1 | 17.2 | 12.1 | 28 | 12.5 | 12.5 | 15.9 | 25 | 14.5 | 20.2 | 43.9 | 55.8 | 71.5 | 77.8 | 63 | 54 | 41 | 1 | 240 | 77.8 | -30.5
KL2-MATA | -16 | -17 | -19 | -19.8 | -14 | -4 | 1.6 | 10.4 | 19.1 | 25.8 | 9.5 | 10.4 | 4.8 | 10 | 13.2 | 17.6 | 12 | 16 | 18 | 24 | 26 | 29 | 43 | 44 | 43 | 32.1 | 3.2 | 10 | 6 | -9 | -10 | 240 | 44 | -19.8
KL1-SYU | -6 | -9 | -10 | -9.4 | -4.6 | -4.1 | -5 | 1.4 | 1.6 | 4.2 | 17.4 | 15.1 | 13.3 | 12 | 1.6 | 0 | 1.7 | -0.41 | 1.8 | -0.6 | 7.6 | 12.9 | 19.4 | 23.2 | 49.9 | 23.2 | 28 | 8 | 4 | 0 | -2 | 60 | 49.9 | -10
KHIMTI-LAMOSANGHU | 81.6 | 88 | 88 | 90 | 88 | 120 | 122 | 135 | 145 | 150 | 135 | 123.984 | 91.84 | 108.24 | 136.612 | 147.272 | 118.08 | 133.12 | 139.36 | 137.6 | 116.8 | 122.88 | 123.2 | 127.2 | 120 | 106.4 | 67.076 | 80 | 75 | 65 | 70 | 120 | 150 | 65
LAMOSHANGU-BHAKTAPUR | 66 | 68 | 69 | 63.6 | 69 | 83.3 | 83.8 | 87.5 | 90.4 | 91.6 | 83.6 | 82.7 | 66.8 | 75 | 87.9 | 92.9 | 83 | 87.5 | 89.5 | 90.9 | 79.7 | 82.9 | 84 | 84.9 | -38.8 | 74.2 | 54 | 59 | 59 | 54 | 65
BALAJU-SYUCHATAR | 50 | 58 | 62 | 54 | 62 | 71.7 | 56.9 | 43.4 | 18.4 | 5.3 | -21.8 | -22.2 | -29 | -6 | 26.1 | 34 | 23.9 | 34.1 | 34.5 | 25.5 | 9.2 | 13 | -0.7 | -24.1 | 66.1 | -47 | -59 | -44 | -24 | -8 | 37
DHALKE-NAWALPUR I | 69 | 72 | 79 | 74.4 | 79.2 | 98 | 99.3 | 101 | 90 | 94.1 | 63.6 | 66.1 | 58 | 84 | 94 | 98.8 | 90 | 94.4 | 94.7 | 94.3 | 79.2 | 84.2 | 88.3 | 88.1 | 65.1 | 50.3 | 31.6 | 54 | 51 | 47 | 68 |  | 101 | 31.6
N. BHARATPUR-BARDGHAT I | 14 | 19 | 19 | 9.2 | 15 | 21.4 | 14 | 13 | 0 | 1.2 | -13.8 | -11.4 | -18 | -7 | 0 | 6.2 | -4 | -1.1 | 0 | -3.1 | 0 | 2.3 | -4.2 | -10 | -18.5 | -21.6 | -24.3 | -23 | -21 | -13 | 11 |  | 21.4 | -24.3
DAMAK-DUHABI | -15 | -15 | -16 | -13 | -14.5 | -17.5 | -24.3 | -36.4 | -47.3 | -52.5 | -49.4 | -49.5 | -44 | -40 | -34.4 | -32.2 | -31 | -31.2 | -35.4 | -41.4 | -45.8 | -51.1 | [10 empty] | -13 | -52.5
HETAUDA-KAMANE | -12 | -15.2 | -15 | -11 | -17.8 | -32 | -31.4 | -31.8 | -27 | -31.5 | 3.2 | 2.7 | 10.6 | -6 | -31.8 | -37 | -24 | -27.4 | -27.4 | -30.9 | -29.1 | -32.9 | -35.8 | -26.6 | -5.6 | -1.4 | 20.7 | -19 | -2 | 12 | -10 |  | 20.7 | -37
MIRCHAIYA LAHAN 2 | 97 | 99 | 94 | 93 | 94.2 | 94.3 | 95.2 | 99.5 | 110 | 109 | 111.6 | 105.4 | 103 | 100 | 120.3 | 116.5 | 117 | 125.6 | 124.1 | 126.9 | 113.6 | 107.6 | 37.7 | 107.4 | 108.6 | 109.2 | 103.4 | 101 | 106 | 110 | 102 |  | 126.9 | 37.7
Water Level
UTK | 1983.81 | 1984.02 | 1984.3 | 1984.5 | 1984.71 | 1984.93 |  | 1985.1 |  | 1985.03 |  | 1984.18 | 1982.95 | 1982.53 | 1982.7 | 1982.79 | 1982.9 | 1983.09 | 1983.2 | 1983.4 | 1983.62 |  | 1983.81 |  | 1983.85 |  | 1982.95 |  | 1982.89 |  | 1983.4
KGA | 520.6 | 520.96 | 521.3 | 521.64 | 521.92 | 522.22 |  | 522.26 |  | 522.1 |  | 521.8 | 521.42 | 521.12 | 521.04 | 520.97 | 520.92 | 520.97 | 521.1 | 521.2 | 521.26 |  | 521.35 |  | 521.02 |  | 520.34 |  |  | 519.226 | 519.35
MMRS | 622.76 | 623.23 | 623.5 | 623.9 | 624.35 | 624.56 |  | 624.83 |  | 624.87 |  | 624.32 | 624.27 | 623.9 | 622.46 | 623.42 | 623.09 | 623.05 | 623.09 | 623.14 | 623.16 |  | 623.18 |  | 623.18 |  | 622.46 |  | 622.06 | 622.06 | 622.2
MRS | 335.51 | 335.9 | 336.21 | 336.54 | 336.77 | 337.03 |  | 337 |  | 336.88 |  | 336.58 | 336.17 | 335.81 | 335.58 | 335.34 | 335.03 | 335.03 | 335.37 | 335.6 | 335.83 |  | 336.07 |  | 336.03 |  | 335.64 |  |  | 335.05
CHM | 884.4 | 885.2 | 885.7 | 886.2 | 886.8 | 887.1 |  | 887.2 |  | 886.4 |  | 885.4 | 885.2 | 885.1 | 885.1 | 885.5 | 886 | 886 | 886.1 | 885.8 | 885.4 |  | 885.3 |  | 884.5 |  | 882.8
KL 1 | 0.29167: 1519.76
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1783.99; 0.041667: 9:00
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/29)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 30
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/30 |  |  | 2080/10/30 |  |  | Wednesday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 684 | 640 | 631.4 | 650.7 | 668.4 | 668.3 | 672.8 | 641.365 | 633.8 | 607.9 | 261.5 | 541.5 | 539.2 | 565.7 | 681.8 | 736.8 | 751.5 | 780.5 | 763.4 | 732 | 594.6 | 582.7 | 437.2 | 349.4 | 466.1 | 379.3 | 519.9 | 529 | 663 | 598.3 | 671
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1680MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=1212 | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1326.69 | 1405.19 | 1491.955 | 1487.69 | 1679.68 | 1596.68 | 1539.88 | 1517.88 | 1384.38 | 1475.28 | 1503.09 | 1505.19 | 1543.79 | 1533.69 | 1548.49 | 1583.29 | 1619.59 | 1753.29 | 1794.39 | 1733.69 | 1623.79 | 1631.89 | 1522.09 | 1336.09 | 1271.69
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1794.39 MW | [29 empty] | Industrial Interruption near (or fed by) Import Points (MW)
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1794.39 MW | [29 empty] | Block | Time | Muzaffarpur | Raxaul | Ramnagar | Sampatiya | Tanakpur | Duhabi | Mirchaiya
Solu Khola Dudhkoshi(86) | 24.4 | 24.4 | 25.4 | 25.4 | 25.4 | 25.4 | 25.1 | 25.1 | 22.6 | 21.9 | 21.9 | 22.4 | 22.4 | 21.8 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 86 | 25.4 | 21.8 | [39 empty] | 1 | 0:00
Likhu-II(55) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 8 | 8 |  | 30 | [37 empty] | 2 | 0:15
Super Dordi (54) | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10 | 10 | 10 | 10 | 10 | 54 | 10.1 | 10 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/30) | [37 empty] | 3 | 0:30
Likhu-IV(52.4) | 11.2 | 11.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 52.4 | 14.2 | 11.2 | [39 empty] | 4 | 0:45
Upper Marsyangdi "A"(50) | 25.2 | 25.2 | 25.3 | 25.3 | 25.3 | 25.3 | 25.4 | 25.4 | 25.4 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 50 | 25.4 | 25.2 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | [9 empty] | 5 | 1:00
Upper Bhotekoshi Khola(45) | 15 | 15 | 17.3 | 17.3 | 17.3 | 17.3 | 16.6 | 16.6 | 16.6 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 45 | 17.3 | 14.9 |  | IPP | 459.45 | 459.45 | 464.75 | 464.75 | 464.75 | 464.75 | 462.95 | 458.95 | 459.45 | 459.45 | 458.85 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 461.35 | 461.35 | 461.35 | 461.35 | 461.35 | [9 empty] | 6 | 1:15
Super Madi ( 44 ) | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44 | 44 | 14 |  | NEA SUB | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 96.2 | 341.2 | 66.2 | 73.1 | 91 | 91 | 96.1 | 76.1 | 91.1 | 76.1 | 86.1 | 51.1 | 66.1 | 267 | 377 | 37 | 37 | 37 | 37 | 97 | 77 | [9 empty] | 7 | 1:30
Mistri Khola(42) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 42 | 7 | 7 |  | NEA ROR PROR | 72.84 | 72.84 | 79.24 | 79.24 | 79.24 | 79.24 | 233.24 | 248.74 | 284.53 | 272.73 | 266.73 | 268.73 | 243.53 | 201.24 | 200.64 | 195.24 | 225.24 | 171.44 | 217.54 | 254.84 | 332.54 | 347.44 | 349.54 | 310.94 | 216.54 | 186.24 | 114.74 | 128.34 | [9 empty] | 8 | 1:45
Upper Chameliya(40) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 38.46 | 11 | 11 |  | IMPORT | 671 | 684 | 640 | 631.4 | 650.7 | 668.4 | 672.8 | 633.8 | 261.5 | 541.5 | 539.2 | 565.7 | 681.8 | 736.8 | 751.5 | 780.5 | 763.4 | 732 | 594.6 | 582.7 | 437.2 | 349.4 | 466.1 | 379.3 | 519.9 | 529 | 663 | 598.3 | [9 empty] | 9 | 2:00
Upper Kalanga Gad(38.46) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.1 | 57 | 57.6 | 61.6 | 72.1 | 85.2 | 47.1 | 8.5 | 0 | 6.7 | [9 empty] | 10 | 2:15
Upper Balefi (36) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 36 | 13 | 13 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 250 | 200 | 180 | 0 | 0 | 10 | 18 | 18 | 10 | 100 | 200 | 200 | 200 | 200 | 350 | 350 | 350 | 300 | 0 | 0 | [9 empty] | 11 | 2:30
Nyadi(30) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 30 | 7.6 | 6.9 |  | System_Load | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1405.19 | 1487.69 | 1596.68 | 1539.88 | 1517.88 | 1384.38 | 1475.28 | 1503.09 | 1505.19 | 1543.79 | 1533.69 | 1548.49 | 1583.29 | 1619.59 | 1753.29 | 1794.39 | 1733.69 | 1623.79 | 1631.89 | 1522.09 | 1336.09 | 1271.69 | 0 | [8 empty] | 12 | 2:45
Likhu Khola A(29.04) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 13 | 3:00
Lower Likhu(28) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 28 | 6.3 | 6.3 |  | National_Load | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1405.19 | 1487.69 | 1596.68 | 1539.88 | 1517.88 | 1384.38 | 1475.28 | 1503.09 | 1505.19 | 1543.79 | 1533.69 | 1548.49 | 1583.29 | 1619.59 | 1753.29 | 1794.39 | 1733.69 | 1623.79 | 1631.89 | 1522.09 | 1336.09 | 1271.69 | 0 | [8 empty] | 14 | 3:15
Dordi(27) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 30 | 9.3 | 9.3 | [39 empty] | 15 | 3:30
Upper Madi(25) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 25 | 8.7 | 8.7 | [39 empty] | 16 | 3:45
Kabeli B-1(25) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5 | [39 empty] | 17 | 4:00
Singati Khola(25) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 25 | 6 | 6 | [39 empty] | 18 | 4:15
Upper Dordi (25) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 25 | 6.6 | 6.6 | [39 empty] | 19 | 4:30
Solu Khola(23.5) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 23.5 | 6.5 | 6.5 | [39 empty] | 20 | 4:45
Upper Chaku A(22.2) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22.2 | 3 | 3 | [39 empty] | 21 | 5:00
Tallo Hewa Khola(22.1) | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 22.1 | 5.5 | 5.5 | [39 empty] | 22 | 5:15
Sanima Mai Khola(22) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 6 | 6 | [39 empty] | 23 | 5:30
Bagmati Khola Small(22) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 22 | 6.1 | 6.1 | [39 empty] | 24 | 5:45
Lower Modi (20) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4 | [39 empty] | 25 | 6:00
Mathilo Solu khola(19.8) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 20 | 4 | 4 | [39 empty] | 26 | 6:15
Middle Modi (18) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 18 | 5.7 | 5.7 | [39 empty] | 27 | 6:30
Kalanga Gad(15.33) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 14.9 | 7.2 | 7.2 | [39 empty] | 28 | 6:45
Hewa Khola A(14.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 0 | 0 | [39 empty] | 29 | 7:00
Sangen(14.8) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14.9 | 5 | 5 | [39 empty] | 30 | 7:15
Ghar khola(14) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14.9 | 4 | 4 | [39 empty] | 31 | 7:30
Thapa Khola(13.6) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 13.6 | 1.8 | 1.8 | [39 empty] | 32 | 7:45
Madkyu Khola(13) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 13 | 3.8 | 3.8 | [39 empty] | 33 | 8:00
Dordi12) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 12 | 7.5 | 7.5 | [39 empty] | 34 | 8:15
Jhimruk Khola(12) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 9 | 9 | [39 empty] | 35 | 8:30
Upper Khimti(12) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 3 | 3 | [39 empty] | 36 | 8:45
Upper Mai Khola (12) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 22 | 3.5 | 3.5 | [39 empty] | 37 | 9:00
Namarjun Madi(11.88) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11.88 | 5 | 5 | [39 empty] | 38 | 9:15
Lower Khare(11) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3 | [39 empty] | 39 | 9:30
Upper Sanigad(10.7) | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 11 | 2.45 | 2.45 | [39 empty] | 40 | 9:45
Down Piluwa(10.3) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 11 | 3 | 3 | [39 empty] | 41 | 10:00
Lower Modi 1(10) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 4 | 4 | [39 empty] | 42 | 10:15
Makari Gad(10.0) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 10 | 4.5 | 4.5 | [39 empty] | 43 | 10:30
Mithila Solar PV Electric Project(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | [39 empty] | 44 | 10:45
Pure-Solar(10) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | [39 empty] | 45 | 11:00
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150 | [39 empty] | 46 | 11:15
Kabeli Corridor | 15.6 | 15.6 | 21.6 | 21.6 | 21.6 | 21.6 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 17.9 | 17.8 | 18.5 | 19.5 | 19.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 240 | 21.6 | 14.3 | [39 empty] | 47 | 11:30
Total IPP | 459.45 | 459.45 | 464.75 | 464.75 | 464.75 | 464.75 | 462.95 | 462.95 | 460.45 | 458.95 | 458.95 | 459.45 | 459.45 | 458.85 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 458.95 | 461.35 | 461.35 | 461.35 | 461.35 | 461.35 | 1042.4 | 464.75 | 458.85 | [39 empty] | 48 | 11:45
Upper Tamakoshi(456) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 60 | 70 | 305 | 30 | 35 | 55 | 55 | 60 | 40 | 55 | 40 | 50 | 15 | 30 | 230 | 340 | 0 | 0 | 0 | 0 | 60 | 40 | 456 | 340 | 0 | [39 empty] | 49 | 12:00
Khimti Khola(60) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 60 | 27 | 27 | [39 empty] | 50 | 12:15
Chilime(22.1) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 11.1 | 9 | 9 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22.1 | 11.1 | 9 | [39 empty] | 51 | 12:30
Total NEA SUBSIDIARIES | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | 66.2 | 96.2 | 106.2 | 341.2 | 66.2 | 73.1 | 91 | 91 | 96.1 | 76.1 | 91.1 | 76.1 | 86.1 | 51.1 | 66.1 | 267 | 377 | 37 | 37 | 37 | 37 | 97 | 77 | 538.1 | 377 | 36.2 | [39 empty] | 52 | 12:45
KGA(144) | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 68.1 | 97.4 | 62.3 | 62 | 71 | 62.2 | 62 | 61.5 | 50 | 40.2 | 48.8 | 48.8 | 67.2 | 61.9 | 88.2 | 111 | 133.8 | 138 | 133.8 | 98 | 61 | 30.5 | 30.5 | 35.5 | 144 | 138 | 0 | [39 empty] | 53 | 13:00 | [5 empty] | 10 | 5
Middle MRS(70) | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 34.4 | 68 | 46.6 | 47.6 | 60 | 59.7 | 49.4 | 49.5 | 49.3 | 29.6 | 23.4 | 23.4 | 35.3 | 0 | 0 | 0 | 23.6 | 34.8 | 47.4 | 47.8 | 25.4 | 25.9 | 0 | 0 | 70 | 68 | 0 | [39 empty] | 54 | 13:15 | [5 empty] | 10 | 5
MRS(69) | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 37 | 70 | 54.2 | 54.2 | 54.8 | 52.5 | 52.1 | 52 | 37.8 | 35 | 35 | 23.4 | 23.1 | 15.8 | 36.8 | 50.6 | 67.8 | 67.5 | 68.4 | 67.3 | 45.9 | 45.6 | 0 | 18 | 69 | 70 | 0 | [39 empty] | 55 | 13:30 | [5 empty] | 10 | 5
U Trisuli 3A(60) | 31.3 | 31.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 36 | 35 | 31 | 34 | 34.3 | 35 | 35 | 35 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3 | 35.2 | 35.2 | 35.2 | 33.7 | 34 | 34 | 34 | 34 | 34 | 60 | 36 | 31 | [39 empty] | 56 | 13:45 | [5 empty] | 10 | 5
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 10.7 | 10.7 | 13.2 | 14.9 | 10.2 | 10.1 | 10.2 | 10.2 | 0 | 0 | 9.5 | 14.7 | 14.7 | 14.5 | 14.3 | 29 | 28.8 | 23.1 | 23 | 9.4 | 9.4 | 9.4 | 0 | 30 | 29 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 57 | 14:00 | [5 empty] | 10 | 5
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 2.8 | 6.7 | 10.3 | 15.3 | 17.7 | 19.1 | 19 | 16 | 12.7 | 7.5 | 1.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19.1 | 0 | [14 empty] | Tanakpur | 55 | 56.8 | 51 | 54.2 | 56.3 | 56.6 | 63 | 44.7 | 49 | 51.2 | 47.8 | 47.4 | 59.6 | 67.5 | 72.4 | 46.3 | 54 | 58.1 | 43.4 | 49.2 | 57 | 62 | 62.3 | 48 | 58 | 14:15 | [5 empty] | 10 | 5
TRI(24) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 16 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 14:30 | [5 empty] | 18 | 5
GDK(15) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 15 | 5 | 4 | [14 empty] | Muz | 400 | 411 | 410 | 426 | 465 | 456 | 416 | 150 | 418.6 | 415 | 434.4 | 433.4 | 457 | 466.5 | 471.5 | 498.2 | 483 | 441.2 | 221.5 | 262 | 385 | 395 | 405 | 402 | 60 | 14:45 | [5 empty] | 18 | 0
DEVI(14.1) | 9 | 9 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 14.1 | 10.6 | 8.3 | [14 empty] | Ram | 39 | 5.6 | 5.4 | 5.2 | 5.1 | 6.6 | 7.9 | 4.8 | 3 | 1 | 7.5 | 32 | 35.4 | 40.5 | 51.8 | 47.3 | 47 | 6.4 | 8 | 6.1 | 23 | 37 | 57 | 39 | 61 | 15:00 | [5 empty] | 18 | 0
MODI(14) | 2.8 | 2.8 | 4.1 | 4.1 | 4.1 | 4.1 | 2.9 | 2.9 | 3 | 2.9 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 14 | 4.1 | 2.8 | [14 empty] | Rax | 140 | 114.6 | 109 | 106.3 | 90 | 84.6 | 78.9 | 0 | 0 | 0 | 0 | 98 | 112.8 | 100 | 99.8 | 98.6 | 88 | 0 | 0 | 0 | 0 | 95 | 0 | 120 | 62 | 15:15 | [5 empty] | 18 | 0
SUN(10.05) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 10.05 | 4.5 | 3 | [14 empty] | Sam | 50 | 52 | 56 | 59 | 52 | 69 | 68 | 62 | 70.9 | 72 | 76 | 71 | 72 | 77 | 85 | 73 | 60 | 77 | 76.5 | 62 | 64 | 74 | 74 | 62 | 63 | 15:30 | [5 empty] | 18 | 0
PUWA(6.2) | 1.7 | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6.2 | 2 | 1.6 | [39 empty] | 64 | 15:45 | [5 empty] | 18 | 0
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 3.54 | 3.54 | [15 empty] | 55 | 56.8 | 51 | 54.2 | 56.3 | 56.6 | 63 | 44.7 | 49 | 51.2 | 47.8 | 47.4 | 59.6 | 67.5 | 72.4 | 46.3 | 54 | 58.1 | 43.4 | 49.2 | 57 | 62 | 62.3 | 48 | 65 | 16:00 | [5 empty] | 10
Total ROR | 72.84 | 72.84 | 79.24 | 79.24 | 79.24 | 79.24 | 159.24 | 233.24 | 323.94 | 248.74 | 256.63 | 284.53 | 272.73 | 266.73 | 268.73 | 243.53 | 201.24 | 200.64 | 195.24 | 225.24 | 171.44 | 217.54 | 254.84 | 332.54 | 347.44 | 349.54 | 310.94 | 216.54 | 186.24 | 114.74 | 128.34 | 489.91 | 349.54 | 72.84 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 16:15 | [5 empty] | 18 | 0
KL1(60) | 0: 0; 0.041667: 0; 0.72917: 44; 0.75: 35; 0.77083: 35; 0.79167: 40; 0.8125: 50; 0.83333: 50; 0.85417: 30; 0.875: 0; 0.91667: 0; 0.95833: 0 | 60 | 50 | 0 | [15 empty] | 400 | 411 | 410 | 426 | 465 | 456 | 416 | 150 | 418.6 | 415 | 434.4 | 433.4 | 457 | 466.5 | 471.5 | 498.2 | 483 | 441.2 | 221.5 | 262 | 385 | 395 | 405 | 402 | 67 | 16:30 | [5 empty] | 10
KL2(32) | 0: 0; 0.041667: 0; 0.72917: 12.5; 0.75: 16.1; 0.77083: 16.6; 0.79167: 15.8; 0.8125: 16.3; 0.83333: 25.8; 0.85417: 12.5; 0.875: 6.2; 0.91667: 0; 0.95833: 5 | 32 | 25.8 | 0 | [15 empty] | 39 | 5.6 | 5.4 | 5.2 | 5.1 | 6.6 | 7.9 | 4.8 | 3 | 1 | 7.5 | 32 | 35.4 | 40.5 | 51.8 | 47.3 | 47 | 6.4 | 8 | 6.1 | 23 | 37 | 57 | 39 | 68 | 16:45 | [5 empty] | 10
KL3(14) | 0: 0; 0.041667: 0; 0.72917: 4.6; 0.75: 5.9; 0.77083: 6; 0.79167: 5.8; 0.8125: 5.8; 0.83333: 9.4; 0.85417: 4.6; 0.875: 2.3; 0.91667: 0; 0.95833: 1.7 | 14 | 9.4 | 0 | [15 empty] | 140 | 114.6 | 109 | 106.3 | 90 | 84.6 | 78.9 | 0 | 0 | 0 | 0 | 98 | 112.8 | 100 | 99.8 | 98.6 | 88 | 0 | 0 | 0 | 0 | 95 | 0 | 120 | 69 | 17:00 | [5 empty] | 10
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.1 | 57 | 57.6 | 61.6 | 72.1 | 85.2 | 47.1 | 8.5 | 0 | 6.7 | 106 | 85.2 | 0 | [15 empty] | 50 | 52 | 56 | 59 | 52 | 69 | 68 | 62 | 70.9 | 72 | 76 | 71 | 72 | 77 | 85 | 73 | 60 | 77 | 76.5 | 62 | 64 | 74 | 74 | 62 | 70 | 17:15 | [5 empty] | 10
TANAKPUR | 48 | 55 | 56.8 | 51 | 54.2 | 56.3 | 54.5 | 56.6 | 50.065 | 63 | 57.9 | 44.7 | 49 | 51.2 | 47.8 | 47.4 | 59.6 | 67.5 | 72.4 | 46.3 | 54 | 55.6 | 58.1 | 47.1 | 43.4 | 54.3 | 49.2 | 66 | 57 | 62 | 62.3 |  | 72.4 | 43.4 | [39 empty] | 71 | 17:30 | [5 empty] | 10
KATAIYA | [32 empty] | 0 | 0 | [39 empty] | 72 | 17:45 | [5 empty] | 30
MUJAFFARPUR | 402 | 400 | 411 | 410 | 426 | 465 | 469 | 456 | 421 | 416 | 418 | 150 | 418.6 | 415 | 434.4 | 433.4 | 457 | 466.5 | 471.5 | 498.2 | 483 | 453.9 | 441.2 | 307.3 | 221.5 | 337.1 | 262 | 386 | 385 | 395 | 405 |  | 498.2 | 150 | [39 empty] | 73 | 18:00 | [5 empty] | 65
RAMNAGAR | 39 | 39 | 5.6 | 5.4 | 5.2 | 5.1 | 5.2 | 6.6 | 7.7 | 7.9 | 7.4 | 4.8 | 3 | 1 | 7.5 | 32 | 35.4 | 40.5 | 51.8 | 47.3 | 47 | 6.1 | 6.4 | 7.8 | 8 | 6.7 | 6.1 | 5.9 | 23 | 37 | 57 |  | 57 | 1 | [22 empty] | 55 | 0 | 400 | 39 | 140 | 50 | [11 empty] | 74 | 18:15 | [5 empty] | 65
RAXAUL 132 | 120 | 140 | 114.6 | 109 | 106.3 | 90 | 91 | 84.6 | 93.6 | 78.9 | 62 |  | 0 | 0 | 0 | 98 | 112.8 | 100 | 99.8 | 98.6 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 |  | 140 | 0 | [22 empty] | 56.8 | 0 | 411 | 5.6 | 114.6 | 52 | [11 empty] | 75 | 18:30 | [5 empty] | 65
NANPARA(33kV) | [32 empty] | 0 | 0 | [22 empty] | 51 | 0 | 410 | 5.4 | 109 | 56 | [11 empty] | 76 | 18:45 | [5 empty] | 65
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [20 empty] | 54.2 | 0 | 426 | 5.2 | 106.3 | 59 | [11 empty] | 77 | 19:00 | [5 empty] | 65
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [22 empty] | 56.3 | 0 | 465 | 5.1 | 90 | 52 | [11 empty] | 78 | 19:15 | [5 empty] | 65
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [21 empty] | 56.6 | 0 | 456 | 6.6 | 84.6 | 69 | [11 empty] | 79 | 19:30 | [5 empty] | 65
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [21 empty] | 63 | 0 | 416 | 7.9 | 78.9 | 68 | [11 empty] | 80 | 19:45 | [5 empty] | 65
SAMPATIYA 132 kV | 62 | 50 | 52 | 56 | 59 | 52 | 48.6 | 69 | 69 | 68 | 62.6 | 62 | 70.9 | 72 | 76 | 71 | 72 | 77 | 85 | 73 | 60 | 79 | 77 | 75 | 76.5 | 68 | 62 | 62 | 64 | 74 | 74 |  | 85 | 48.6 | [22 empty] | 44.7 | 0 | 150 | 4.8 | 0 | 62 | [11 empty] | 81 | 20:00 | [5 empty] | 65
Total IMPORT | 671 | 684 | 640 | 631.4 | 650.7 | 668.4 | 668.3 | 672.8 | 641.365 | 633.8 | 607.9 | 261.5 | 541.5 | 539.2 | 565.7 | 681.8 | 736.8 | 751.5 | 780.5 | 763.4 | 732 | 594.6 | 582.7 | 437.2 | 349.4 | 466.1 | 379.3 | 519.9 | 529 | 663 | 598.3 | 0 | 780.5 | 261.5 | [22 empty] | 49 | 0 | 418.6 | 3 | 0 | 70.9 | [11 empty] | 82 | 20:15 | [5 empty] | 65
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [22 empty] | 51.2 | 0 | 415 | 1 | 0 | 72 | [11 empty] | 83 | 20:30 | [5 empty] | 65
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [22 empty] | 47.8 | 0 | 434.4 | 7.5 | 0 | 76 | [11 empty] | 84 | 20:45 | [5 empty] | 65
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [22 empty] | 47.4 | 0 | 433.4 | 32 | 98 | 71 | [11 empty] | 85 | 21:00
Total THERMAL | 0: 0; 0.041667: 0 | 55.4 | 0 | 0 | [22 empty] | 59.6 | 0 | 457 | 35.4 | 112.8 | 72 | [11 empty] | 86 | 21:15
TOTAL SYSTEM LOAD (ACTUAL) | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1326.69 | 1405.19 | 1491.955 | 1437.69 | 1429.68 | 1346.68 | 1339.88 | 1337.88 | 1384.38 | 1475.28 | 1493.09 | 1487.19 | 1525.79 | 1523.69 | 1448.49 | 1383.29 | 1419.59 | 1553.29 | 1594.39 | 1383.69 | 1273.79 | 1281.89 | 1222.09 | 1336.09 | 1271.69 | 2231.81 | 1594.39 | 1211.59 | [22 empty] | 67.5 | 0 | 466.5 | 40.5 | 100 | 77 | [11 empty] | 87 | 21:30
Interruption/Tripping | 0 | 0 | [7 empty] | 50 | 250 | 250 | 200 | 180 |  |  | 10 | 18 | 18 | 10 | 100 | 200 | 200 | 200 | 200 | 350 | 350 | 350 | 300 |  |  |  | 350 | 0 | [22 empty] | 72.4 | 0 | 471.5 | 51.8 | 99.8 | 85 | [11 empty] | 88 | 21:45
TOTAL SYSTEM LOAD (EXPECTED) | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1326.69 | 1405.19 | 1491.955 | 1487.69 | 1679.68 | 1596.68 | 1539.88 | 1517.88 | 1384.38 | 1475.28 | 1503.09 | 1505.19 | 1543.79 | 1533.69 | 1548.49 | 1583.29 | 1619.59 | 1753.29 | 1794.39 | 1733.69 | 1623.79 | 1631.89 | 1522.09 | 1336.09 | 1271.69 | 1693.71 | 1794.39 | 1211.59 | [22 empty] | 46.3 | 0 | 498.2 | 47.3 | 98.6 | 73 | [11 empty] | 89 | 22:00
TOTAL NATIONAL LOAD (ACTUAL) | 1239.49 | 1252.49 | 1220.19 | 1211.59 | 1230.89 | 1248.59 | 1326.69 | 1405.19 | 1491.955 | 1487.69 | 1679.68 | 1596.68 | 1539.88 | 1517.88 | 1384.38 | 1475.28 | 1503.09 | 1505.19 | 1543.79 | 1533.69 | 1548.49 | 1583.29 | 1619.59 | 1753.29 | 1794.39 | 1733.69 | 1623.79 | 1631.89 | 1522.09 | 1336.09 | 1271.69 |  | 1794.39 | 1211.59 | [22 empty] | 54 | 0 | 483 | 47 | 88 | 60 | [11 empty] | 90 | 22:15
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 58.1 | 0 | 441.2 | 6.4 | 0 | 77 | [11 empty] | 91 | 22:30
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 43.4 | 0 | 221.5 | 8 | 0 | 76.5 | [11 empty] | 92 | 22:45
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 49.2 | 0 | 262 | 6.1 | 0 | 62 | [11 empty] | 93 | 23:00
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 57 | 0 | 385 | 23 | 0 | 64 | [11 empty] | 94 | 23:15
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 62 | 0 | 395 | 37 | 95 | 74 | [11 empty] | 95 | 23:30
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 62.3 | 0 | 405 | 57 | 0 | 74 | [11 empty] | 96 | 23:45
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [22 empty] | 48 | 0 | 402 | 39 | 120 | 62
NET IMPORT | 671 | 684 | 640 | 631.4 | 650.7 | 668.4 | 668.3 | 672.8 | 641.365 | 633.8 | 607.9 | 261.5 | 541.5 | 539.2 | 565.7 | 681.8 | 736.8 | 751.5 | 780.5 | 763.4 | 732 | 594.6 | 582.7 | 437.2 | 349.4 | 466.1 | 379.3 | 519.9 | 529 | 663 | 598.3 |  | 780.5 | 261.5
HZ | 50.04 | 49.98 | 50.01 | 49.918 | 49.918 | 49.977 | 49.923 | 50.007 | 50.081 | 49.928 | 49.85 | 49.884 | 50.011 | 50.078 | 50.062 | 50.055 | 49.99 | 49.97 | 49.93 | 49.96 | 50 | 50 | 50.04 | 49.92 | 49.95 | 50 | 49.96 | 50.035 | 49.976 | 50.002 | 50.025 |  | 50.081 | 49.85
HTD 132KV | 130.4 | 130.4 | 130.2 | 129.8 | 129.8 | 127.1 | 127.3 | 127.3 | 127 | 128.2 | 126 | 124.7 | 124.3 | 126.6 | 124 | 125.1 | 124.1 | 125.3 | 122.2 | 124.6 | 127.2 | 127.2 | 129 | 127 | 127.5 | 130.7 | 131.2 | 130.3 | 130.1 | 128.6 | 127.8 |  | 131.2 | 122.2
SUI 132KV | 133 | 133 | 133.6 | 133.2 | 133.2 | 130.6 | 130.8 | 130.8 | 129.6 | 130 | 127.6 | 127.5 | 127.8 | 129 | 128 | 128.2 | 127.2 | 128.6 | 126.1 | 127.8 | 129.8 | 129.8 | 131.74 | 131.74 | 129.4 | 132.3 | 132.5 | 132.2 | 132.4 | 131.7 | 132 |  | 133.6 | 126.1
DUBI 132KV | 0.58333: 125.4; 0.625: 127.8; 0.66667: 124.2; 0.70833: 127.3; 0.72917: 127.3; 0.75: 128.8; 0.77083: 128.8; 0.79167: 129.31; 0.8125: 133.1; 0.83333: 131.1; 0.85417: 129.4; 0.875: 128.7; 0.91667: 126.1; 0.95833: 128.5 |  | 133.1 | 124.2
ANAMANI 132KV | 133 | 134 | 134.6 | 134.5 | 134.5 | 130.6 | 128.7 | 128.7 | 122.2 | 122.6 | 122.4 | 122.6 | 123.3 | 125.6 | 121.5 | 127.4 | 122.3 | 123.9 | 126.3 | 123.9 | 125.9 | 125.9 | 125.8 | 125.8 | 127.3 | 131.4 | 131.5 | 130.8 | 129.7 | 128.3 | 131 |  | 134.6 | 121.5
KG-A 132KV | 134.5 | 131.4 | 133.9 | 133.9 | 133.9 | 131.8 | 132.8 | 135.1 | 133.9 | 136.2 | 133.5 | 132.9 | 131.9 | 132.2 | 121.7 | 133.3 | 131.2 | 135.3 | 130.6 | 134.3 | 135.2 | 135.2 | 135.5 | 135.5 | 135.8 | 136.9 | 135.8 | 136.5 | 136.7 | 133.2 | 133.4 |  | 136.9 | 121.7
KOHALPUR 132KV | 134.6 | 131.5 | 132.6 | 136.9 | 136.9 | 130.6 | 127.2 | 129.3 | 132.3 | 132 | 135.2 | 130 | 130.9 | 131.5 | 131.5 | 131.2 | 131 | 128.8 | 126.9 | 130.6 | 135.7 | 135.7 | 133.7 | 133.7 | 129.1 | 130.6 | 133.9 | 134.8 | 133.4 | 133.9 | 131.7 |  | 136.9 | 126.9
SUI 66KV | 67 | 66.9 | 67.2 | 67 | 67 | 65.6 | 65.8 | 65.6 | 65.1 | 65.3 | 64.2 | 64.1 | 64.2 | 64.8 | 64.1 | 64.3 | 63.7 | 65 | 65 | 64.2 | 65.3 | 65.3 | 66.5 | 66.5 | 65 | 66.5 | 66.2 | 66.1 | 66.2 | 66.1 | 66.2 |  | 67.2 | 63.7
[33 empty] | 0 | 0
Kathmandu Load | 120.84 | 112.84 | 130.824 | 127.916 | 161.54 | 163.864 | 185.612 | 226.124 | 276.712 | 194.54 | 345.476 | 331.692 | 315.54 | 308.94 | 42 | 293.2 | 238.04 | 274.6 | 279.94 | 284.32 | 287.66 | 286.66 | 319.54 | 371.08 | 396.92 | 363.84 | 292.1 | 286.608 | 268.34 | 206.94 | 158.94 |  | 396.92 | 42
MRS-SYU | -4 | -11 | -14.2 | -14.1 | -13.2 | -16.9 | -3.5 | 14 | 32.4 | 24.4 | 24.8 | 33.9 | 28.9 | 28.9 | 31.3 | 18.2 | 12.6 | 22.1 | 12.8 | 17 | 15.1 | 15.1 | 31.1 | 40.8 | 32.1 | 50.5 | 45.9 | 29.8 | 30.7 | 3.9 | 10.1 | 75 | 50.5 | -16.9
NMRS-MATA | -11 | -18 | -22.4 | -23.1 | -24.2 | -26.8 | -8.8 | 14.4 | 38.8 | 34.2 | 35.2 | 48.7 | 42.7 | 42.3 | 39.2 | 20.5 | 11.5 | 23.2 | 12.6 | 18.8 | 16.7 | 16.7 | 38.3 | 51.6 | 38.8 | 64.6 | 57.4 | 34.8 | 35.2 | -0.2 | 8.6 | 240 | 64.6 | -26.8
KL2-MATA | -12 | -10 | -12.3 | -13.2 | -6.1 | 0 | 0 | 0 | 5.6 | 34.2 | 39.5 | 21.2 | 13.6 | 7.8 | 2.6 | 14 | 16.6 | 9.3 | 16 | 17 | 29 | 29 | 21 | 26 | 42.9 | 43 | 1 | 15.6 | 18 | 5 | -33 | 240 | 43 | -33
KL1-SYU | -10 | -11 | -11.8 | -13.7 | -6 | -10.2 | -8 | -6.1 | 2.5 | 17.5 | 17.9 | 16.7 | 14.1 | 12.8 | 5.8 | 5.5 | 5.7 | -4.8 | -2 | 2.9 | 6.7 | 6.7 | 32.6 | 35.3 | 41.9 | 49.6 | 52.5 | 26.5 | 16 | -0.2 | -5.4 | 60 | 52.5 | -13.7
KHIMTI-LAMOSANGHU | 75 | 80 | 103.484 | 103.976 | 123 | 129.724 | 118.572 | 115.784 | 110.372 |  | 139.236 | 118.152 | 118.9 | 114.8 | 123 | 129.56 | 86.4 | 122.56 | 141.6 | 134.88 | 132.32 | 132.32 | 108.8 | 130.24 | 154.08 | 70.5 | 51.66 | 96.268 | 84.8 | 114.8 | 95 | 120 | 154.08 | 51.66
LAMOSHANGU-BHAKTAPUR | 72 | 74 | 74.1 | 75 | 82.2 | 87.7 | 84 | 79.2 | 76.3 | 85.6 | 90.3 | 81.4 | 79.3 | 77.7 | 80.1 | 85.2 | 90.9 | 81.6 | 92.5 | 87.6 | 86.9 | 86.9 | 74.6 | 84.9 | 96.1 | 56.6 | 46.4 | 70.1 | 65 | 80 | 72
BALAJU-SYUCHATAR | 52 | 54 | 59.4 | 62 | 63 | 64.8 | 52.2 | 26.3 | -4.6 | -11.7 | -11.7 | -16.7 | -7.8 | -2.3 | 6 | 23.7 | 35.8 | 25.2 | 36.2 | 26.4 | 20.5 | 20.5 | -11.2 | -21.2 | -14.9 | -60.7 | -58.5 | -70.5 | -12 | 38 | 47
DHALKE-NAWALPUR I | 81 | 85 | 79.2 | 86.4 | 95 | 101.4 | 95.2 | 84.8 | 80.4 | 82.7 | 95.6 | 92.9 | 86 | 84.9 | 92.8 | 88.5 | 98.7 | 82.5 | 103.4 | 91.2 | 91.4 | 91.4 | 83.5 | 85.5 | 95.9 | 49 | 34.9 | 76.6 | 67 | 80 | 90 |  | 103.4 | 34.9
N. BHARATPUR-BARDGHAT I | 12 | 20 | 23.4 | 23.8 | 25.1 | 25 | 18.2 | 6.7 | 0 | 3.7 | 1 | -3.9 | -1.3 | -1.3 | 4.8 | 4.4 | 6.2 | -7.1 | -3.6 | -5.1 | -4.6 | -4.6 | -11.1 | -14.8 | -6.4 | -15.9 | -9.1 | 0 | 0 | 1.6 | -1.8 |  | 25.1 | -15.9
DAMAK-DUHABI | 0.58333: -36.7; 0.625: -29.5; 0.66667: -42.5; 0.70833: -49.5; 0.72917: -49.5; 0.75: -61; 0.79167: -66.3; 0.8125: -56; 0.83333: -43.2; 0.85417: -37.5; 0.875: -34; 0.91667: -24; 0.95833: -18 |  | -18 | -66.3
HETAUDA-KAMANE | -17 | -21 | -22.4 | -24.1 | -37.1 | -36.8 | -30.4 | -20.4 | -11.5 | -31.4 | -32.9 | -9.6 | -9.4 | -6.4 | -8.6 | -22.9 | -31.4 | -18.7 | -29.3 | -23.2 | -37.8 | -37.8 | 1.3 | 2.7 | -13.9 | 6.6 | 16.4 | -14.8 | -6 | -20 | -19 |  | 16.4 | -37.8
MIRCHAIYA LAHAN 2 | 98 | 92 | 91 | 90.7 | 96 | 95 | 98.5 | 108.5 | 113.5 | 107.8 | 114.9 | 109.7 | 102.1 | 102 | 116.2 | 119.3 | 125.7 | 126.2 | 119.8 | 123.5 | 123.5 | 123.5 | 109.9 | 124.6 | 118.4 | 100 | 65.6 | 95.4 | 102 | 111 | 109 |  | 126.2 | 65.6
Water Level
UTK | 1983.65 | 1983.9 | 1984.15 | 1984.35 | 1984.55 | 1984.75 |  | 1984.95 |  | 1985.03 |  | 1984.97 | 1984.82 | 1984.9 | 1984.95 | 1984.98 | 1985.06 | 1985.09 | 1985.15 | 1985.2 | 1985.21 |  | 1985.31 | [5 empty] | 1985.5 | 1985.75 | 1985.55
KGA | 519.76 | 520.14 | 520.48 | 520.82 | 521.14 | 521.46 |  | 521.6 |  | 521.38 |  | 521.32 | 521.18 | 521.12 | 521.05 | 520.99 | 521.05 | 521.08 | 521.1 | 521.02 | 520.87 |  | 520.663 |  | 519.58 |  | 519.48 |  | 519.38 | 519.56 | 519.72
MMRS | 622.71 | 623.12 | 623.51 | 623.85 | 624.16 | 624.52 |  | 624.56 |  | 624.22 |  | 624.09 | 623.99 | 623.03 | 622.67 | 622.18 |  | 621.7 | 621.81 | 621.66 | 621.63 |  | 622.38 |  | 622.47 |  | 621.98 |  | 622 | 622.72 | 622.73
MRS | 334.99 | 335.52 | 336 | 336.3 | 336.59 | 336.83 |  | 336.95 |  | 336.68 |  | 336.32 | 335.94 | 335.56 | 335.15 | 334.57 |  | 334.6 | 335.88 | 335.16 | 335.45 |  | 335.68 |  | 335.47 |  | 335.09 |  | 334.77 | 334.72 | 334.98
CHM | 884.8 | 885.4 | 885.9 | 886.5 | 886.9 | 887.3 |  | 887.4 |  | 887.4 |  | 887.1 | 887 | 886.9 | 886.9 | 886.8 |  | 887.2 | 887.6 | 887.4 | 887.2 |  | 887 |  | 886 |  | 885 |  | 885.7 | 884.7 | 884.7
KL 1 | 0: 1519.75
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 0: 1679.68; 0.041667: 7:30
PEAK SUMMARY | 0.083333: Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/30)
IPP | bar: 0
NEA(RoR+PRoR) | bar: 0
KL1+KL2+KL3 | bar: 0
Import | bar: 0
Export | bar: 0
Total | bar: 0
Time | bar: 0
Frequency | bar: 0
Note on A2: Load Supply Group

## 31
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | 2080/10/31 |  |  | 2080/10/31 |  |  | Thursday |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 581 | 575 | 565.4 | 579.3 | 613.4 | 653.3 | 655.3 | 593.2 | 340.1 | 217 | 118.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 1625MW at 7:30hr | [21 empty] | 1638.31 | Total Hydro
Base Load=154 | 1295.79 | 1244.29 | 1238.29 | 1242.19 | 1256.09 | 1290.19 | 1327.39 | 1404.19 | 1556.58 | 1443.59 | 1625.49 | 1595.69 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 1595.69 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 1595.69 MW
Solu Khola Dudhkoshi(86) | 0: 24.4; 0.041667: 24.4; 0.083333: 24.4; 0.125: 25.4; 0.16667: 25.4; 0.20833: 25.4; 0.22917: 24.6; 0.25: 24.6; 0.27083: 23.7; 0.29167: 23.7; 0.3125: 23.7; 0.33333: 24.8 | 86 | 25.4 | 23.7
Likhu-II(55) | 0: 8; 0.041667: 8; 0.083333: 8; 0.125: 8; 0.16667: 8; 0.20833: 8; 0.22917: 8; 0.25: 8; 0.27083: 8; 0.29167: 8; 0.3125: 8; 0.33333: 8 | 54 | 8 | 8 |  | 31
Super Dordi (54) | 0: 10; 0.041667: 10; 0.083333: 10; 0.125: 10; 0.16667: 10; 0.20833: 10; 0.22917: 10; 0.25: 10; 0.27083: 10; 0.29167: 9.4; 0.3125: 9.4; 0.33333: 9.4 | 54 | 10 | 9.4 |  | Daily Load Curve(Excluding of Export) of Nepal (Nepali Date: 2080/10/31)
Likhu-IV(52.4) | 0: 14.2; 0.041667: 14.2; 0.083333: 14.2; 0.125: 14.2; 0.16667: 14.2; 0.20833: 14.2; 0.22917: 13.4; 0.25: 13.4; 0.27083: 13.4; 0.29167: 13.5; 0.3125: 13.5; 0.33333: 13.5 | 52.4 | 14.2 | 13.4
Upper Marsyangdi "A"(50) | 0: 25.2; 0.041667: 25.2; 0.083333: 25.2; 0.125: 25.2; 0.16667: 25.2; 0.20833: 25.2; 0.22917: 25.3; 0.25: 25.3; 0.27083: 25.3; 0.29167: 25.3; 0.3125: 25.3; 0.33333: 28.1 | 50 | 28.1 | 25.2 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | 0: 14.9; 0.041667: 14.9; 0.083333: 14.9; 0.125: 14.9; 0.16667: 14.9; 0.20833: 14.9; 0.22917: 15.9; 0.25: 15.9; 0.27083: 14.8; 0.29167: 14.8; 0.3125: 14.8; 0.33333: 13.7 | 45 | 15.9 | 13.7 |  | IPP | 461.35 | 461.35 | 461.35 | 462.35 | 462.35 | 462.35 | 461.85 | 459.35 | 451.75 | 150 | 150 | 150
Super Madi ( 44 ) | 0: 14; 0.041667: 14; 0.083333: 14; 0.125: 14; 0.16667: 14; 0.20833: 14; 0.22917: 14; 0.25: 14; 0.27083: 14; 0.29167: 14; 0.3125: 14; 0.33333: 14 | 44 | 44 | 14 |  | NEA SUB | 62.1 | 77.1 | 77.1 | 87.1 | 87.1 | 87.1 | 67.1 | 237.1 | 387.1 | 0 | 0 | 0
Mistri Khola(42) | 0: 7; 0.041667: 7; 0.083333: 7; 0.125: 7; 0.16667: 7; 0.20833: 7; 0.22917: 7; 0.25: 7; 0.27083: 7; 0.29167: 7; 0.3125: 7; 0.33333: 7 | 42 | 7 | 7 |  | NEA ROR PROR | 128.34 | 74.84 | 74.84 | 77.34 | 77.34 | 77.34 | 169.94 | 357.04 | 351.94 | 3.54 | 3.54 | 3.54
Upper Chameliya(40) | 0: 11; 0.041667: 11; 0.083333: 11; 0.125: 11; 0.16667: 11; 0.20833: 11; 0.22917: 11; 0.25: 11; 0.27083: 11; 0.29167: 11; 0.3125: 11; 0.33333: 11 | 38.46 | 11 | 11 |  | IMPORT | 594 | 581 | 575 | 565.4 | 579.3 | 613.4 | 655.3 | 340.1 | 118.2 | 0 | 0 | 0
Upper Kalanga Gad(38.46) | 0: 7.8; 0.041667: 7.8; 0.083333: 7.8; 0.125: 7.8; 0.16667: 7.8; 0.20833: 7.8; 0.22917: 7.8; 0.25: 7.8; 0.27083: 7.8; 0.29167: 7.8; 0.3125: 7.8; 0.33333: 7.8 | 38.46 | 7.8 | 7.8 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7 | 0 | 0 | 0
Upper Balefi (36) | 0: 13; 0.041667: 13; 0.083333: 13; 0.125: 13; 0.16667: 13; 0.20833: 13; 0.22917: 13; 0.25: 13; 0.27083: 13; 0.29167: 13; 0.3125: 13; 0.33333: 13 | 36 | 13 | 13 |  | INTERRUPTION | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 250 | 0 | 0 | 0
Nyadi(30) | 0: 6.9; 0.041667: 6.9; 0.083333: 6.9; 0.125: 6.9; 0.16667: 6.9; 0.20833: 6.9; 0.22917: 6.9; 0.25: 6.9; 0.27083: 6.9; 0.29167: 6.9; 0.3125: 6.9; 0.33333: 7.5 | 30 | 7.5 | 6.9 |  | System_Load | 1295.79 | 1244.29 | 1238.29 | 1242.19 | 1256.09 | 1290.19 | 1404.19 | 1443.59 | 1595.69 | 153.54 | 153.54 | 153.54
Likhu Khola A(29.04) | 0: 5.5; 0.041667: 5.5; 0.083333: 5.5; 0.125: 5.5; 0.16667: 5.5; 0.20833: 5.5; 0.22917: 5.5; 0.25: 5.5; 0.27083: 5.5; 0.29167: 5.5; 0.3125: 5.5; 0.33333: 5.5 | 24.2 | 5.5 | 5.5 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | 0: 6.3; 0.041667: 6.3; 0.083333: 6.3; 0.125: 6.3; 0.16667: 6.3; 0.20833: 6.3; 0.22917: 6.3; 0.25: 6.3; 0.27083: 6.3; 0.29167: 6.3; 0.3125: 6.3; 0.33333: 6.4 | 28 | 6.4 | 6.3 |  | National_Load | 1295.79 | 1244.29 | 1238.29 | 1242.19 | 1256.09 | 1290.19 | 1404.19 | 1443.59 | 1595.69 | 153.54 | 153.54 | 153.54
Dordi(27) | 0: 9.3; 0.041667: 9.3; 0.083333: 9.3; 0.125: 9.3; 0.16667: 9.3; 0.20833: 9.3; 0.22917: 9.3; 0.25: 9.3; 0.27083: 9.3; 0.29167: 9.3; 0.3125: 9.3; 0.33333: 5.9 | 30 | 9.3 | 5.9
Upper Madi(25) | 0: 8.7; 0.041667: 8.7; 0.083333: 8.7; 0.125: 8.7; 0.16667: 8.7; 0.20833: 8.7; 0.22917: 8.7; 0.25: 8.7; 0.27083: 8.7; 0.29167: 8.7; 0.3125: 8.7; 0.33333: 6.7 | 25 | 8.7 | 6.7
Kabeli B-1(25) | 0: 5; 0.041667: 5; 0.083333: 5; 0.125: 5; 0.16667: 5; 0.20833: 5; 0.22917: 5; 0.25: 5; 0.27083: 5; 0.29167: 5; 0.3125: 5; 0.33333: 5 | 25 | 5 | 5
Singati Khola(25) | 0: 6; 0.041667: 6; 0.083333: 6; 0.125: 6; 0.16667: 6; 0.20833: 6; 0.22917: 6; 0.25: 6; 0.27083: 6; 0.29167: 6; 0.3125: 6; 0.33333: 6 | 25 | 6 | 6
Upper Dordi (25) | 0: 6.6; 0.041667: 6.6; 0.083333: 6.6; 0.125: 6.6; 0.16667: 6.6; 0.20833: 6.6; 0.22917: 6.6; 0.25: 6.6; 0.27083: 6.6; 0.29167: 6.6; 0.3125: 6.6; 0.33333: 6.2 | 25 | 6.6 | 6.2
Solu Khola(23.5) | 0: 6.5; 0.041667: 6.5; 0.083333: 6.5; 0.125: 6.5; 0.16667: 6.5; 0.20833: 6.5; 0.22917: 6.5; 0.25: 6.5; 0.27083: 6.5; 0.29167: 6.5; 0.3125: 6.5; 0.33333: 5.6 | 23.5 | 6.5 | 5.6
Upper Chaku A(22.2) | 0: 3; 0.041667: 3; 0.083333: 3; 0.125: 3; 0.16667: 3; 0.20833: 3; 0.22917: 3; 0.25: 3; 0.27083: 3; 0.29167: 3; 0.3125: 3; 0.33333: 3 | 22.2 | 3 | 3
Tallo Hewa Khola(22.1) | 0: 5.5; 0.041667: 5.5; 0.083333: 5.5; 0.125: 5.5; 0.16667: 5.5; 0.20833: 5.5; 0.22917: 5.5; 0.25: 5.5; 0.27083: 5.5; 0.29167: 5.5; 0.3125: 5.5; 0.33333: 5.5 | 22.1 | 5.5 | 5.5
Sanima Mai Khola(22) | 0: 6; 0.041667: 6; 0.083333: 6; 0.125: 6; 0.16667: 6; 0.20833: 6; 0.22917: 6; 0.25: 6; 0.27083: 6; 0.29167: 6; 0.3125: 6; 0.33333: 6 | 22 | 6 | 6
Bagmati Khola Small(22) | 0: 6.1; 0.041667: 6.1; 0.083333: 6.1; 0.125: 6.1; 0.16667: 6.1; 0.20833: 6.1; 0.22917: 6.1; 0.25: 6.1; 0.27083: 6.1; 0.29167: 6.1; 0.3125: 6.1; 0.33333: 6.7 | 22 | 6.7 | 6.1
Lower Modi (20) | 0: 4; 0.041667: 4; 0.083333: 4; 0.125: 4; 0.16667: 4; 0.20833: 4; 0.22917: 4; 0.25: 4; 0.27083: 4; 0.29167: 4; 0.3125: 4; 0.33333: 4 | 20 | 4 | 4
Mathilo Solu khola(19.8) | 0: 4; 0.041667: 4; 0.083333: 4; 0.125: 4; 0.16667: 4; 0.20833: 4; 0.22917: 4; 0.25: 4; 0.27083: 4; 0.29167: 4; 0.3125: 4; 0.33333: 4 | 20 | 4 | 4
Middle Modi (18) | 0: 5.7; 0.041667: 5.7; 0.083333: 5.7; 0.125: 5.7; 0.16667: 5.7; 0.20833: 5.7; 0.22917: 5.7; 0.25: 5.7; 0.27083: 5.7; 0.29167: 5.7; 0.3125: 5.7; 0.33333: 5.7 | 18 | 5.7 | 5.7
Kalanga Gad(15.33) | 0: 7.2; 0.041667: 7.2; 0.083333: 7.2; 0.125: 7.2; 0.16667: 7.2; 0.20833: 7.2; 0.22917: 7.2; 0.25: 7.2; 0.27083: 7.2; 0.29167: 7.2; 0.3125: 7.2; 0.33333: 7.2 | 14.9 | 7.2 | 7.2
Hewa Khola A(14.9) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0 | 14.9 | 0 | 0
Sangen(14.8) | 0: 5; 0.041667: 5; 0.083333: 5; 0.125: 5; 0.16667: 5; 0.20833: 5; 0.22917: 5; 0.25: 5; 0.27083: 5; 0.29167: 5; 0.3125: 5; 0.33333: 5 | 14.9 | 5 | 5
Ghar khola(14) | 0: 4; 0.041667: 4; 0.083333: 4; 0.125: 4; 0.16667: 4; 0.20833: 4; 0.22917: 4; 0.25: 4; 0.27083: 4; 0.29167: 4; 0.3125: 4; 0.33333: 4 | 14.9 | 4 | 4
Thapa Khola(13.6) | 0: 1.8; 0.041667: 1.8; 0.083333: 1.8; 0.125: 1.8; 0.16667: 1.8; 0.20833: 1.8; 0.22917: 1.8; 0.25: 1.8; 0.27083: 1.8; 0.29167: 1.8; 0.3125: 1.8; 0.33333: 1.8 | 13.6 | 1.8 | 1.8
Madkyu Khola(13) | 0: 3.8; 0.041667: 3.8; 0.083333: 3.8; 0.125: 3.8; 0.16667: 3.8; 0.20833: 3.8; 0.22917: 3.8; 0.25: 3.8; 0.27083: 3.8; 0.29167: 3.8; 0.3125: 3.8; 0.33333: 3.8 | 13 | 3.8 | 3.8
Dordi12) | 0: 7.5; 0.041667: 7.5; 0.083333: 7.5; 0.125: 7.5; 0.16667: 7.5; 0.20833: 7.5; 0.22917: 7.5; 0.25: 7.5; 0.27083: 7.5; 0.29167: 7.5; 0.3125: 7.5; 0.33333: 2.5 | 12 | 7.5 | 2.5
Jhimruk Khola(12) | 0: 9; 0.041667: 9; 0.083333: 9; 0.125: 9; 0.16667: 9; 0.20833: 9; 0.22917: 9; 0.25: 9; 0.27083: 9; 0.29167: 9; 0.3125: 9; 0.33333: 9 | 12 | 9 | 9
Upper Khimti(12) | 0: 3; 0.041667: 3; 0.083333: 3; 0.125: 3; 0.16667: 3; 0.20833: 3; 0.22917: 3; 0.25: 3; 0.27083: 3; 0.29167: 3; 0.3125: 3; 0.33333: 3 | 12 | 3 | 3
Upper Mai Khola (12) | 0: 3.5; 0.041667: 3.5; 0.083333: 3.5; 0.125: 3.5; 0.16667: 3.5; 0.20833: 3.5; 0.22917: 3.5; 0.25: 3.5; 0.27083: 3.5; 0.29167: 3.5; 0.3125: 3.5; 0.33333: 3.5 | 22 | 3.5 | 3.5
Namarjun Madi(11.88) | 0: 5; 0.041667: 5; 0.083333: 5; 0.125: 5; 0.16667: 5; 0.20833: 5; 0.22917: 5; 0.25: 5; 0.27083: 5; 0.29167: 5; 0.3125: 5; 0.33333: 5 | 11.88 | 5 | 5
Lower Khare(11) | 0: 3; 0.041667: 3; 0.083333: 3; 0.125: 3; 0.16667: 3; 0.20833: 3; 0.22917: 3; 0.25: 3; 0.27083: 3; 0.29167: 3; 0.3125: 3; 0.33333: 3 | 11 | 3 | 3
Upper Sanigad(10.7) | 0: 2.45; 0.041667: 2.45; 0.083333: 2.45; 0.125: 2.45; 0.16667: 2.45; 0.20833: 2.45; 0.22917: 2.45; 0.25: 2.45; 0.27083: 2.45; 0.29167: 2.45; 0.3125: 2.45; 0.33333: 2.45 | 11 | 2.45 | 2.45
Down Piluwa(10.3) | 0: 3; 0.041667: 3; 0.083333: 3; 0.125: 3; 0.16667: 3; 0.20833: 3; 0.22917: 3; 0.25: 3; 0.27083: 3; 0.29167: 3; 0.3125: 3; 0.33333: 3 | 11 | 3 | 3
Lower Modi 1(10) | 0: 4; 0.041667: 4; 0.083333: 4; 0.125: 4; 0.16667: 4; 0.20833: 4; 0.22917: 4; 0.25: 4; 0.27083: 4; 0.29167: 4; 0.3125: 4; 0.33333: 4 | 10 | 4 | 4
Makari Gad(10.0) | 0: 4.5; 0.041667: 4.5; 0.083333: 4.5; 0.125: 4.5; 0.16667: 4.5; 0.20833: 4.5; 0.22917: 4.5; 0.25: 4.5; 0.27083: 4.5; 0.29167: 4.5; 0.3125: 4.5; 0.33333: 4.5 | 10 | 4.5 | 4.5
Mithila Solar PV Electric Project(10) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0 | 10 | 0 | 0
Pure-Solar(10) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 0; 0.27083: 0; 0.29167: 0; 0.3125: 0; 0.33333: 0 | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | 0: 14.3; 0.041667: 14.3; 0.083333: 14.3; 0.125: 21.4; 0.16667: 21.4; 0.20833: 21.4; 0.22917: 18.7; 0.25: 18.3; 0.27083: 18.4; 0.29167: 18.2; 0.3125: 18.2; 0.33333: 16 | 240 | 21.4 | 14.3
Total IPP | 461.35 | 461.35 | 461.35 | 462.35 | 462.35 | 462.35 | 461.85 | 461.85 | 459.85 | 459.35 | 459.35 | 451.75 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1042.4 | 462.35 | 150
Upper Tamakoshi(456) | 0: 25; 0.041667: 40; 0.083333: 40; 0.125: 50; 0.16667: 50; 0.20833: 50; 0.22917: 35; 0.25: 30; 0.27083: 110; 0.29167: 200; 0.3125: 305; 0.33333: 350 | 456 | 350 | 25
Khimti Khola(60) | 0: 27; 0.041667: 27; 0.083333: 27; 0.125: 27; 0.16667: 27; 0.20833: 27; 0.22917: 27; 0.25: 27; 0.27083: 27; 0.29167: 27; 0.3125: 27; 0.33333: 27 | 60 | 27 | 27
Chilime(22.1) | 0: 10.1; 0.041667: 10.1; 0.083333: 10.1; 0.125: 10.1; 0.16667: 10.1; 0.20833: 10.1; 0.22917: 10.1; 0.25: 10.1; 0.27083: 10.1; 0.29167: 10.1; 0.3125: 10.1; 0.33333: 10.1 | 22.1 | 10.1 | 10.1
Total NEA SUBSIDIARIES | 62.1 | 77.1 | 77.1 | 87.1 | 87.1 | 87.1 | 72.1 | 67.1 | 147.1 | 237.1 | 342.1 | 387.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538.1 | 387.1 | 0
KGA(144) | 0: 35.5; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 30.3; 0.27083: 98.4; 0.29167: 121; 0.3125: 121; 0.33333: 142.2 | 144 | 142.2 | 0
Middle MRS(70) | 0: 0; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 24.8; 0.27083: 48.3; 0.29167: 69; 0.3125: 69; 0.33333: 53.7 | 70 | 69 | 0
MRS(69) | 0: 18; 0.041667: 0; 0.083333: 0; 0.125: 0; 0.16667: 0; 0.20833: 0; 0.22917: 0; 0.25: 14.9; 0.27083: 58.39; 0.29167: 69; 0.3125: 69; 0.33333: 50.9 | 69 | 69 | 0
U Trisuli 3A(60) | 0: 34; 0.041667: 34; 0.083333: 34; 0.125: 35.3; 0.16667: 35.3; 0.20833: 35.3; 0.22917: 35.3; 0.25: 35.3; 0.27083: 35.2; 0.29167: 35.2; 0.3125: 35.2; 0.33333: 36 | 60 | 36 | 34
CHM(30) | 0 | 0 | 0 | 0 | 0 | 0 | 14.9 | 24.7 | 26.3 | 23 | 23 | 23.4 | [19 empty] | 30 | 26.3 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.4 | 6.4 | [19 empty] | 25 | 6.4 | 0 | [14 empty] | Tanakpur | 60 | 58 | 61 | 51.2 | 48 | 58 | 65.7 | 50.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65
TRI(24) | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [19 empty] | 24 | 16 | 15 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [19 empty] | 15 | 4 | 4 | [14 empty] | Muz | 411 | 401 | 392 | 411 | 446 | 471 | 204 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402
DEVI(14.1) | 8.3 | 8.3 | 8.3 | 10.2 | 10.2 | 10.2 | 9.7 | 9.7 | 9.2 | 9.2 | 9.2 | 9.5 | [19 empty] | 14.1 | 10.2 | 8.3 | [14 empty] | Ram | 50 | 54 | 52.3 | 54.8 | 58.4 | 59.3 | 8.4 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49
MODI(14) | 4 | 4 | 4 | 4.3 | 4.3 | 4.3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.3 | [19 empty] | 14 | 4.3 | 2.3 | [14 empty] | Rax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUN(10.05) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [19 empty] | 10.05 | 3 | 3 | [14 empty] | Sam | 60 | 62 | 60.1 | 62.3 | 61 | 67 | 62 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78
PUWA(6.2) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [19 empty] | 6.2 | 2 | 2
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 60 | 58 | 61 | 51.2 | 48 | 58 | 65.7 | 50.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65
Total ROR | 128.34 | 74.84 | 74.84 | 77.34 | 77.34 | 77.34 | 90.14 | 169.94 | 306.43 | 357.04 | 357.04 | 351.94 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 489.91 | 357.04 | 3.5 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [11 empty] | 20 | [19 empty] | 60 | 20 | 20 | [15 empty] | 411 | 401 | 392 | 411 | 446 | 471 | 204 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402
KL2(32) | [11 empty] | 12.2 | [19 empty] | 32 | 12.2 | 12.2 | [15 empty] | 50 | 54 | 52.3 | 54.8 | 58.4 | 59.3 | 8.4 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49
KL3(14) | [11 empty] | 4.5 | [19 empty] | 14 | 4.5 | 4.5 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 36.7 | 0 | [15 empty] | 60 | 62 | 60.1 | 62.3 | 61 | 67 | 62 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78
TANAKPUR | 65 | 60 | 58 | 61 | 51.2 | 48 | 62 | 58 | 65 | 65.7 | 57 | 50.3 | [20 empty] | 65.7 | 48
KATAIYA | 0 | [31 empty] | 0 | 0
MUJAFFARPUR | 402 | 411 | 401 | 392 | 411 | 446 | 465 | 471 | 412 | 204 | 91 | 2 | [20 empty] | 471 | 2
RAMNAGAR | 49 | 50 | 54 | 52.3 | 54.8 | 58.4 | 54.3 | 59.3 | 54.2 | 8.4 | 7 | 5.9 | [20 empty] | 59.3 | 5.9 | [15 empty] | 8: 60; 9: 0; 10: 411; 11: 50; 12: 0; 13: 60
RAXAUL 132 | 0 | [31 empty] | 0 | 0 | [15 empty] | 8: 58; 9: 0; 10: 401; 11: 54; 12: 0; 13: 62
NANPARA(33kV) | 0 | [31 empty] | 0 | 0 | [15 empty] | 8: 61; 9: 0; 10: 392; 11: 52.3; 12: 0; 13: 60.1
BISHANPUR(33kV) | 0 | [31 empty] | 0 | 0 |  | UTK Discharge Test | [13 empty] | 8: 51.2; 9: 0; 10: 411; 11: 54.8; 12: 0; 13: 62.3
JALESHWOR(33kV) | 0 | [31 empty] | 0 | 0 | [15 empty] | 8: 48; 9: 0; 10: 446; 11: 58.4; 12: 0; 13: 61
RAJBIRAJ(33kV) | 0 | [31 empty] | 0 | 0 | Line1 | [14 empty] | 8: 58; 9: 0; 10: 471; 11: 59.3; 12: 0; 13: 67
RAXAUL(33kV) | 0 | [31 empty] | 0 | 0 | Line 2 | [14 empty] | 8: 65.7; 9: 0; 10: 204; 11: 8.4; 12: 0; 13: 62
SAMPATIYA 132 kV | 78 | 60 | 62 | 60.1 | 62.3 | 61 | 72 | 67 | 62 | 62 | 62 | 60 | [20 empty] | 78 | 60 | [15 empty] | 8: 50.3; 9: 0; 10: 2; 11: 5.9; 12: 0; 13: 60
Total IMPORT | 594 | 581 | 575 | 565.4 | 579.3 | 613.4 | 653.3 | 655.3 | 593.2 | 340.1 | 217 | 118.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655.3 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Total THERMAL | [22 empty] | 0 | [8 empty] | 55.4 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL SYSTEM LOAD (ACTUAL) | 1245.79 | 1194.29 | 1188.29 | 1192.19 | 1206.09 | 1240.19 | 1277.39 | 1354.19 | 1506.58 | 1393.59 | 1375.49 | 1345.69 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 2231.81 | 1506.58 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Interruption/Tripping | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 250 | 250 | [20 empty] | 250 | 50 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL SYSTEM LOAD (EXPECTED) | 1295.79 | 1244.29 | 1238.29 | 1242.19 | 1256.09 | 1290.19 | 1327.39 | 1404.19 | 1556.58 | 1443.59 | 1625.49 | 1595.69 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 1693.71 | 1625.49 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL NATIONAL LOAD (ACTUAL) | 1295.79 | 1244.29 | 1238.29 | 1242.19 | 1256.09 | 1290.19 | 1327.39 | 1404.19 | 1556.58 | 1443.59 | 1625.49 | 1595.69 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 |  | 1625.49 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 65; 9: 0; 10: 402; 11: 49; 12: 0; 13: 78
NET IMPORT | 594 | 581 | 575 | 565.4 | 579.3 | 613.4 | 653.3 | 655.3 | 593.2 | 340.1 | 217 | 118.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 655.3 | 0
HZ | 50.005 | 49.943 | 49.943 | 50.016 | 49.9851 | 49.982 | 49.9 | 49.965 | 49.95 | 50.005 | 50.005 | 50.07 | [20 empty] | 50.07 | 49.9
HTD 132KV | 128.6 | 127.2 | 128.6 | 129 | 127.9 | 126.3 | 125.2 | 126 | 125.3 | 126 | 126 | 128 | [20 empty] | 129 | 125.2
SUI 132KV | 132.8 | 131.6 | 132.9 | 133.1 | 132.3 | 131 | 129.6 | 129.8 | 128.7 | 128.1 | 128.1 | 129.5 | [20 empty] | 133.1 | 128.1
DUBI 132KV | 130.9 | 127.9 | 129.7 | 126.3 | 126.8 | 126.5 | 126 | 120.8 | 126.1 | 125.1 | 125.1 | 128.5 | [20 empty] | 130.9 | 120.8
ANAMANI 132KV | 133.3 | 131.9 | 132.1 | 130.2 | 130.8 | 129.9 | 127.7 | 123 | 126.1 | 122.2 | 122.2 | 125.4 | [20 empty] | 133.3 | 122.2
KG-A 132KV | 135.7 | 134.1 | 135.1 | 13.1 | 135 | 136.2 | 134.9 | 134.9 | 132.3 | 131.2 | 131.2 | 134.4 | [20 empty] | 136.2 | 13.1
KOHALPUR 132KV | 129.1 | 129.4 | 134.2 | 128.8 | 132.2 | 125 | 125.1 | 128.6 | 124.5 | 131.3 | 131.3 | 128.9 | [20 empty] | 134.2 | 124.5
SUI 66KV | 66.8 | 66 | 66.8 | 66.9 | 66.6 | 65.7 | 65 | 65 | 64.6 | 64.3 | 64.3 | 65.1 | [20 empty] | 66.9 | 64.3
[33 empty] | 0 | 0
Kathmandu Load | 133.94 | 106.54 | 114.84 | 127.212 | 129.652 | 169.504 | 181.2 | 225.752 | 283.28 | 333.82 | 333.82 | 292.84 | 0.94 | 0.94 | 42 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0 | 0 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 |  | 333.82 | 0
MRS-SYU | 7.6 | -0.6 | -0.8 | 0.3 | -0.6 | 1.4 | 0.8 | 14 | 39.3 | 50 | 50 | 42.5 | [19 empty] | 75 | 50 | -0.8
NMRS-MATA | 5.7 | -4.5 | -4.8 | -3.3 | -3.5 | -2.1 | -3.7 | 13.7 | 48.2 | 72 | 72 | 61.3 | [19 empty] | 240 | 72 | -4.8
KL2-MATA | -38 | -42 | -36 | -40 | -42.5 | -25.8 | -21.2 | -13.1 | -10.6 | 9 | 9 | 14.2 | [19 empty] | 240 | 14.2 | -42.5
KL1-SYU | -5 | -10 | -9.2 | -9.6 | -9.3 | -4.8 | -5.5 | 1.5 | 8.9 | 16 | 16 | 26.1 | [19 empty] | 60 | 26.1 | -10
KHIMTI-LAMOSANGHU | 80 | 80 | 82 | 93.972 | 99.712 | 114.964 | 125.46 | 124.312 | 112.34 | 101.68 | 101.68 | 55.9 | [19 empty] | 120 | 125.46 | 55.9
LAMOSHANGU-BHAKTAPUR | 66.9 | 75 | 70 | 69.2 | 71.7 | 78.8 | 83.5 | 83.2 | 76.2 | 71 | 71 | 65.6 | [20 empty] | 83.5 | 65.6
BALAJU-SYUCHATAR | 50 | 67 | 60 | 59.1 | 63.9 | 55.5 | 57.3 | 36.5 | -3.3 | -40 | -40 | -39.6 | [20 empty] | 67 | -40
DHALKE-NAWALPUR I | 88.9 | 101 | 84 | 91 | 97.7 | 103.5 | 111.2 | 101.2 | 89 | 60 | 60 | 45 | [20 empty] | 111.2 | 45
N. BHARATPUR-BARDGHAT I | 1.3 | 3.7 | 5.3 | 3.5 | 3.7 | 0 | 0 | -3.9 | -16.9 | -13 | -13 | -14.1 | [20 empty] | 5.3 | -16.9
DAMAK-DUHABI | -19 | -16 | -16 | -13.6 | -15.2 | -23 | -25.7 | -35.1 | -47.5 | -57 | -57 | -52.1 | [20 empty] | -13.6 | -57
HETAUDA-KAMANE | 18.1 | 16 | 12 | 17.6 | 16.3 | 6.8 | 0 | 3.5 | 20.6 | 14 | 14 | 16.1 | [20 empty] | 20.6 | 0
MIRCHAIYA LAHAN 2 | 95.6 | 100 | 100 | 103.4 | 101.3 | 99.3 | 101 | 112 | 125 | 110 | 110 | 93.2 | [20 empty] | 125 | 93.2
Water Level
UTK | 1985.65 | 1985.75 | 1985.8 | 1985.9 | 1986 | 1986.1 |  | 1986.2 |  | 1986.14 |  | 1985.75
KGA | 519.87 | 520.23 | 520.58 | 520.93 | 521.24 | 521.54 |  | 521.78 |  | 521.62 |  | 521..06
MMRS | 623.27 | 623.65 | 623.95 | 624.22 | 624.51 | 624.93 |  | 625.1 |  | 624.92 |  | 624.4
MRS | 335.08 | 335.23 | 335.57 | 335.88 | 336.14 | 336.4 |  | 336.45 |  | 336.3 |  | 335.7
CHM | 885.4 | 885.8 | 886.3 | 886.8 | 887.3 | 887.5 |  | 887 | 885.9 |  |  | 885.1
KL 1 | 1519.71
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 1625.49 | 7:30
PEAK SUMMARY |  |  | Pie Chart of Daily Peak Demand(Inclusive of Export) of Nepal (Nepali Date: 2080/10/31)
IPP
NEA(RoR+PRoR)
KL1+KL2+KL3
Import
Export
Total
Time
Frequency
Note on A2: Load Supply Group

## NSample
LOAD DISPATCH CENTRE, NEPAL ELECTRICITY AUTHORITY DAILY SYSTEM OPERATION LOG FOR INPS | [31 empty] | Installed Capacity (MW)
| Bhai |  | Sim |  | Ktm |  | Brt |  | Rainfall | Bhai | Sim | Ktm | Brt | [18 empty] | 1042.4 | IPP
[21 empty] | * other ipp reduced to 210 due to addition of rudi khola a in log sheet |  | llkkjmj | [8 empty] | 489.91 | NEA RoR
Nepali Date: | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | Total Peak Supply(Inclusive of Export) (0 MW) IPP = 0 MW NEA RoR = 0 MWImport = 0 MW KL1+KL2+K3 = 0 MW EXPORT = 0 | [21 empty] | 106 | NEA Storage
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Evening Peak 0MW at 0:0hr at 0Hz Morning Peak 154MW at 4:60hr | [21 empty] | 1638.31 | Total Hydro
Base Load=154 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54
| Night Shift(Contd..) | [10 empty] | Morning Shift | [5 empty] | Day Shift | [8 empty] | Night Shift | [16 empty] | DAILY SYSTEM PEAK : 153.54 MW
Hrs. Source | 0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833 | Installed Capacity (MW) | [11 empty] | DAILY NATIONAL PEAK : 153.54 MW
Solu Khola Dudhkoshi(86) | [31 empty] | 86 | 0 | 0
Likhu-II(55) | [31 empty] | 54 | 0 | 0 |  | NSample
Super Dordi (54) | [31 empty] | 54 | 0 | 0 |  | #VALUE!
Likhu-IV(52.4) | [31 empty] | 52.4 | 0 | 0
Upper Marsyangdi "A"(50) | [31 empty] | 50 | 0 | 0 |  | Hrs. | 0:00 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25 | 0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833
Upper Bhotekoshi Khola(45) | [31 empty] | 45 | 0 | 0 |  | IPP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Super Madi ( 44 ) | [31 empty] | 44 | 44 | 44 |  | NEA SUB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mistri Khola(42) | [31 empty] | 42 | 0 | 0 |  | NEA ROR PROR | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54
Upper Chameliya(40) | [31 empty] | 38.46 | 0 | 0 |  | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Kalanga Gad(38.46) | [31 empty] | 38.46 | 0 | 0 |  | NEA STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Balefi (36) | [31 empty] | 36 | 0 | 0 |  | INTERRUPTION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyadi(30) | [31 empty] | 30 | 0 | 0 |  | System_Load | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54
Likhu Khola A(29.04) | [31 empty] | 24.2 | 0 | 0 |  | Export | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Likhu(28) | [31 empty] | 28 | 0 | 0 |  | National_Load | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54
Dordi(27) | [31 empty] | 30 | 0 | 0
Upper Madi(25) | [31 empty] | 25 | 0 | 0
Kabeli B-1(25) | [31 empty] | 25 | 0 | 0
Singati Khola(25) | [31 empty] | 25 | 0 | 0
Upper Dordi (25) | [31 empty] | 25 | 0 | 0
Solu Khola(23.5) | [31 empty] | 23.5 | 0 | 0
Upper Chaku A(22.2) | [31 empty] | 22.2 | 0 | 0
Tallo Hewa Khola(22.1) | [31 empty] | 22.1 | 0 | 0
Sanima Mai Khola(22) | [31 empty] | 22 | 0 | 0
Bagmati Khola Small(22) | [31 empty] | 22 | 0 | 0
Lower Modi (20) | [31 empty] | 20 | 0 | 0
Mathilo Solu khola(19.8) | [31 empty] | 20 | 0 | 0
Middle Modi (18) | [31 empty] | 18 | 0 | 0
Kalanga Gad(15.33) | [31 empty] | 14.9 | 0 | 0
Hewa Khola A(14.9) | [31 empty] | 14.9 | 0 | 0
Sangen(14.8) | [31 empty] | 14.9 | 0 | 0
Ghar khola(14) | [31 empty] | 14.9 | 0 | 0
Thapa Khola(13.6) | [31 empty] | 13.6 | 0 | 0
Madkyu Khola(13) | [31 empty] | 13 | 0 | 0
Dordi12) | [31 empty] | 12 | 0 | 0
Jhimruk Khola(12) | [31 empty] | 12 | 0 | 0
Upper Khimti(12) | [31 empty] | 12 | 0 | 0
Upper Mai Khola (12) | [31 empty] | 22 | 0 | 0
Namarjun Madi(11.88) | [31 empty] | 11.88 | 0 | 0
Lower Khare(11) | [31 empty] | 11 | 0 | 0
Upper Sanigad(10.7) | [31 empty] | 11 | 0 | 0
Down Piluwa(10.3) | [31 empty] | 11 | 0 | 0
Lower Modi 1(10) | [31 empty] | 10 | 0 | 0
Makari Gad(10.0) | [31 empty] | 10 | 0 | 0
Mithila Solar PV Electric Project(10) | [31 empty] | 10 | 0 | 0
Pure-Solar(10) | [31 empty] | 10 | 0 | 0
Other IPP Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 85 | 150 | 150
Kabeli Corridor | [31 empty] | 240 | 0 | 0 | bar: 0 to 0.27083; 0.77083 to 0.95833
Total IPP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1042.4 | 150 | 150
Upper Tamakoshi(456) | [31 empty] | 456 | 0 | 0 | bar: 0.375 to 0.70833
Khimti Khola(60) | [31 empty] | 60 | 0 | 0
Chilime(22.1) | [31 empty] | 22.1 | 0 | 0
Total NEA SUBSIDIARIES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538.1 | 0 | 0
KGA(144) | [31 empty] | 144 | 0 | 0
Middle MRS(70) | [31 empty] | 70 | 0 | 0
MRS(69) | [31 empty] | 69 | 0 | 0
U Trisuli 3A(60) | [31 empty] | 60 | 0 | 0 | bar: 0.29167 to 0.3125
CHM(30) | [31 empty] | 30 | 0 | 0 | [15 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
NEA SOLAR(25) | [31 empty] | 25 | 0 | 0 | [14 empty] | Tanakpur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRI(24) | [31 empty] | 24 | 0 | 0 | [14 empty] | Kat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GDK(15) | [31 empty] | 15 | 0 | 0 | [14 empty] | Muz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVI(14.1) | [31 empty] | 14.1 | 0 | 0 | [14 empty] | Ram | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MODI(14) | [31 empty] | 14 | 0 | 0 | [14 empty] | Rax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUN(10.05) | [31 empty] | 10.05 | 0 | 0 | [14 empty] | Sam | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUWA(6.2) | [31 empty] | 6.2 | 0 | 0
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56 | 5.5 | 3.5 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total ROR | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.5 | 5.5 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 489.91 | 5.5 | 3.5 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL1(60) | [31 empty] | 60 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL2(32) | [31 empty] | 32 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KL3(14) | [31 empty] | 14 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total STORGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TANAKPUR | [32 empty] | 0 | 0
KATAIYA | [32 empty] | 0 | 0
MUJAFFARPUR | [32 empty] | 0 | 0
RAMNAGAR | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAXAUL 132 | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
NANPARA(33kV) | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
BISHANPUR(33kV) | [32 empty] | 0 | 0 |  | UTK Discharge Test | [13 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
JALESHWOR(33kV) | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAJBIRAJ(33kV) | [32 empty] | 0 | 0 | Line1 | [14 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAXAUL(33kV) | [32 empty] | 0 | 0 | Line 2 | [14 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
SAMPATIYA 132 kV | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Total IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MULTI F(39) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
HTD DIE(14.41) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MRS DI() | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Total THERMAL | [22 empty] | 0 | [8 empty] | 55.4 | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL SYSTEM LOAD (ACTUAL) | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 2231.81 | 155.5 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Interruption/Tripping | [32 empty] | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL SYSTEM LOAD (EXPECTED) | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 1693.71 | 155.5 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TOTAL NATIONAL LOAD (ACTUAL) | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.5 | 155.5 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 | 153.54 |  | 155.5 | 153.5 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAMNAGAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
KATAIYA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
RAXAUL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
MUZAFFARPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
TANAKPUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
OTHERS EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
Total EXPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [15 empty] | 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0
NET IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HZ | [32 empty] | 0 | 0
HTD 132KV | [32 empty] | 0 | 0
SUI 132KV | [32 empty] | 0 | 0
DUBI 132KV | [32 empty] | 0 | 0
ANAMANI 132KV | [32 empty] | 0 | 0
KG-A 132KV | [32 empty] | 0 | 0
KOHALPUR 132KV | [32 empty] | 0 | 0
SUI 66KV | [32 empty] | 0 | 0
[33 empty] | 0 | 0
Kathmandu Load | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 42 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0 | 0 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 |  | 42 | 0
MRS-SYU | [31 empty] | 75 | 0 | 0
NMRS-MATA | [31 empty] | 240 | 0 | 0
KL2-MATA | [31 empty] | 240 | 0 | 0
KL1-SYU | [31 empty] | 60 | 0 | 0
KHIMTI-LAMOSANGHU | [31 empty] | 120 | 0 | 0
LAMOSHANGU-BHAKTAPUR
BALAJU-SYUCHATAR
DHALKE-NAWALPUR I | [32 empty] | 0 | 0
N. BHARATPUR-BARDGHAT I | [32 empty] | 0 | 0
DAMAK-DUHABI | [32 empty] | 0 | 0
HETAUDA-KAMANE | [32 empty] | 0 | 0
MIRCHAIYA LAHAN 2 | [32 empty] | 0 | 0
Water Level
UTK
KGA
MMRS
MRS
CHM
KL 1
Others IPP Detail
Upper Mai Khola(9.98) | [31 empty] | 9.94
Kabeli B-1 Cascade(9.94)
Iwa Khola(9.9)
Sipring Khola(9.658)
Super Mai 'A' (9.6)
Mai Beni(9.51)
Andhi Khola(9.4)
Rudi Khola A(8.8)
Naugadh gad Khola(8.5)
Butwal Solar Project(8.5)
Upper Hewa Khola Small(8.5)
Ankhu Khola - 1(8.4)
Mai sana Cascade(8)
Upper Naugad Gad(8)
Taksar Pikhuwa(8)
Super Mai(7.8)
Jogmai(7.6) | [31 empty] | 9.9
Indrawati - III (7.5) | [31 empty] | 9.658
Upper Khorunga(7.5) | [31 empty] | 9.6
Mai Cascade(7) | [31 empty] | 9.51
Molung Khola(7) | [31 empty] | 9.4
Upper Mardi(7) | [31 empty] | 8.8
Upper Khimti II(7) | [31 empty] | 8.5
Rudi Khola B(6.6) | [31 empty] | 8.5
Sapsup Khola(6.6) | [31 empty] | 8.4
Suri Khola(6.4) | [31 empty] | 8
Lower Jogmai(6.2) | [31 empty] | 8
Daraudi Khola A(6) | [31 empty] | 8
Upper Mai C(5.1) | [31 empty] | 7.8
Tadi Khola (Thaprek)(5) | [31 empty] | 7.6
Mailung Khola(5) | [31 empty] | 7.5
Upper Hugdi Khola(5) | [31 empty] | 7.5
Pikhuwa Khola(5) | [31 empty] | 7
Ghalemdi Khola(5) | [31 empty] | 7
Ghatte Khola(5) | [31 empty] | 7
Belchautara Solar Project(5) | [31 empty] | 7
Lower Tadi(4.993) | [31 empty] | 6.6
Richet Khola(4.98) | [31 empty] | 6.6
Siuri Khola(4.95) | [31 empty] | 6.4
Phawa Khola(4.95) | [31 empty] | 6
Mardi Khola(4.8) | [31 empty] | 5.1
Padam Khola(4.8) | [31 empty] | 5
Mai Khola(4.5) | [31 empty] | 5
Bijayapur 2 Khola Small(4.5) | [31 empty] | 5
Hewa Khola(4.455) | [31 empty] | 5
Bijayapur-1(4.41) | [31 empty] | 5
Radhi Khola(4.4) | [31 empty] | 5
Tungun-Thosne(4.36) | [31 empty] | 5
Baramchi Khola(4.2) | [31 empty] | 4.993
Khudi Khola(4) | [31 empty] | 4.98
Sabha Khola(4) | [31 empty] | 4.95
Puwa Khola -1 (4) | [31 empty] | 4.95
Sardi Khola(4) | [31 empty] | 4.8
Chandranigahpur Solar Project(4) | [31 empty] | 4.8
Upper Chhyangdi Khola(4) | [31 empty] | 4.8
Super Mai Cascade(3.8) | [31 empty] | 4.5
Dwari Khola(3.75) | [31 empty] | 4.5
Charanawati Khola(3.52) | [31 empty] | 4.455
Kapadi Gad(3.33) | [31 empty] | 4.41
Piluwa Khola Small(3) | [31 empty] | 4.4
Chaku Khola(3) | [31 empty] | 4.36
Bhairab Kunda(3) | [31 empty] | 4.2
Upper Puwa -1(3) | [31 empty] | 4
Midim Karapu(3) | [31 empty] | 4
Upper Rawa(3) | [31 empty] | 4
Everest Sugar and Chemical Industries Ltd.(3) | [31 empty] | 4
Indushankar Chini Udhyog Ltd.(3) | [31 empty] | 4
Dhalkebar Solar Project(3) | [31 empty] | 4
Chake Khola(2.83) | [31 empty] | 4
Sunkoshi Small(2.5) | [31 empty] | 4
Daram Khola A(2.5) | [31 empty] | 3.75
Ridi Khola(2.4) | [31 empty] | 3.52
Upper Syange Khola(2.4) | [31 empty] | 3.33
Jiri Khola Small(2.2) | [31 empty] | 3.2
Chhandi(2) | [31 empty] | 3
Jhyadi Khola(2) | [31 empty] | 3
Khani Khola(2) | [31 empty] | 3
Middle Chaku(1.8) | [31 empty] | 3
Lower Chaku Khola(1.8) | [31 empty] | 3
Thoppal Khola(1.65) | [31 empty] | 3
Theule Khola(1.5) | [31 empty] | 3
Dhalkebar Saurya Aayojana(1) | [31 empty] | 3
Suspa Bukhari(0.998) | [31 empty] | 2.83
Lower Chhote Khola(0.997) | [31 empty] | 2.5
Hadi Khola Sunkoshi A(0.997) | [31 empty] | 2.5
Pati Khola Small(0.996) | [31 empty] | 2.4
Miya Khola(0.996) | [31 empty] | 2.4
Jeuligad(0.996) | [31 empty] | 2.2
Pheme Khola(0.995) | [31 empty] | 2
Chhote Khola(0.993) | [31 empty] | 2
Upper Hadi Khola(0.991) | [31 empty] | 2
Lower Piluwa Small(0.99) | [31 empty] | 1.8
Seti-II(0.979) | [31 empty] | 1.8
Bishnu Priya Solar Farm Project(0.96) | [31 empty] | 1.65
Sisne Khola Small(0.75) | [31 empty] | 1.5
Solar(0.68) | [31 empty] | 0.998
Dhunge-Jiri(0.6) | [31 empty] | 0.997
Belkhu(0.518) | [31 empty] | 0.997
Rairang Khola(0.5) | [31 empty] | 0.996
Sali Nadi(0.25) | [31 empty] | 0.996
Syange Khola(0.183) | [31 empty] | 0.996
Midim Khola(0.1) | [31 empty] | 0.995
Sobuwa Khola-2 MHP(0.09) | [31 empty] | 0.993
Leguwa Khola(0.04) | [31 empty] | 0.99
Syauri Bhumey(0.023) | [31 empty] | 0.979
Others IPP Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.723
Other NEA Small
PANAUTI(2.4) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.4
TATOPANI(2) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 2
SETI(1.5) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
FEWA(1) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1
TINAU(1) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1
SUNDARIJAL(0.66) | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.66
Other NEA Small | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 8.56
Morning Peak | 153.54 | 5:00
PEAK SUMMARY |  |  | #VALUE!
IPP
NEA(RoR+PRoR)
KL1+KL2+KL3
Import
Export
Total
Time
Frequency
Note on A2: Load Supply Group

## Sheet1
Name | Class
aaa | class1
bbb | class2
abc | class1
dsfasd | class2
sdf | class2
sdfsd | class4
sdf | class3
SSD
ESD
TRP

## Praveen
Syule | 60171
Upper Kalangad 38 | 60176 | 19.3
Kalanga Gad_15.33 | 60175 | 12
Upper Sanigad 10.70 | 60174 | 5.7
Upper Chameliya_ | 60173 | 26 | [11 empty] | 16
API Darchula 8 |  | 5 | [10 empty] | ind | 8 | 2 feeder
|  | 83 | [10 empty] | purano | 11 kV | 125
[7 empty] | L likhu | 638400 |  |  |  |  | labipur
[13 empty] | Mainya | 2 fed | light
[14 empty] | 1 fed | 8-9 MW
KGA(144) | [8 empty] | 82.835 |  |  |  |  | 45 MVA
Middle MRS(70) | 70
MRS(69) | 69 | [11 empty] | Butwal | Argach
U Trisuli 3A(60) | 60 | [10 empty] | 304 |  | Dhagdhagi | 300 Amp | 2 feeders of 33 kV
CHM(30) | 30
TRI(24) | 14.8 | [11 empty] | Sunwal | palpa+goyal | 10 MW | 2.5 domes
GDK(15) | [13 empty] | Sarb shut
DEVI(14.1) | 13 | [12 empty] | laxmi | 1 mw
MODI(14) | 14 | [12 empty] | Goyal | 5 mw
SUN(10.05)
PUWA(6.2)
|  | 90% | 80% | 75% | 75% | 20%
Nyadi | 30 | 27 | 24 | 22.5 | 22.5 | 6 | 22.5 |  |  | mistri | 40 |  | Upper Sanigad | 60174 | 56 |  | Likhu2 | 60086
Sdordi | 13 | 13 | 13 | 13 | 13 | 8 | 0 |  |  | ghalemdi | 5 |  | Upper Chameliya | 60173
udordi | 25 | 22.5 | 20 | 18.75 | 18.75 | 5 | 14.35 |  |  | ghar khola | 14
dordi27 | 27 | 24.3 | 21.6 | 20.25 | 20.25 | 5.4 | 13.2 |  |  | lmodi1 | 10
dordi 12 | 12 | 10.8 | 9.6 | 9 | 9 | 2.4 | 6.5 |  |  | lmodi20 | 20
Chepe | 8.6 | 7.74 | 6.88 | 6.45 | 6.45 | 1.72 | 7.5 | 8 |  |  | 89
Dordi Corridor Total | 115.6 | 105.34 | 71.08 | 67.45 | 67.45 | 22.52 | 64.05
26.1
[6 empty] | Dordi NyadiSpill | 37.95
Mistri | [5 empty] | KGA | 40
[6 empty] | MMRS | 15
L Modi | 11 |  |  |  |  | MRS | 35
L Modi-1 | [5 empty] | Ghar |  |  |  |  | 304
Middle Modi | 9.5 | 5.5 |  |  |  | Ghalamdi |  |  | Date: 9 | Load at 0730 | 1361 | DAM at 0730 | 350 | UTK at 0730 | 456
Ghalamdi_5 | 2.5 |  |  |  |  | L-Modi |  |  |  | Load at 4 | 991 | DAM at 0400 | 300 | UTK at 0400 | 65
Ghar Khola_14 | 7.5 | 4 |  |  |  | M-Modi |  |  |  | increase in Load | 370 | Export Increase | 50 | UTK Increase | 391
IdiMardi
Super Madi | 60084 | [8 empty] | UTK Increase
Upper Madi | 17551 | [8 empty] | KGA Increase
Namarjun_12 | 10.5 | [8 empty] | MMRS Increase
Sikless_13 | 9.5 | 9.5
IdiMardi_7 | 2
Likhu-A | 60092
L-Likhu
Khimti
Likhu-IV | 60091
Likhu 2 | 60086
BKPC
Balephi
Singati | 17
Sipring_9.6 | 4 | [6 empty] | 121
Ghatte_5 | 2.4 | [6 empty] | 10.5
| Spill | [6 empty] | 84
14
U Solu_23.5 | 60093 | [6 empty] | 12
Solu86 | 60087 | [5 empty] | - | 3.1
Kohalpur | Ambe on Tr2m voltage on left
238.4
Sunwal | 20 MW
Butwal | 45 MW | Shree Steel | [5 empty] | MRS-SYU
Mainya | 12 MW | half load | 40 MW | Full load |  |  |  | NMRS-MATA
KL2-MATA
Lamahi | Ashok Steels
Shivpur | Bijaya Cement | 25 at peak | 7.2 after industry shutdown |  |  |  |  | KL1-SYU
| Vijay Steel | [6 empty] | KHIMTI-LAMOSAGU
Parwani-Het
Parwani-Simra Ckt#1 | Jagadamba Enterprises
Jagadamba Wire_14MW
Parwani-Birjung-1 | Sarbottam | Birg1:
UTK
17:41
22
Godak | Sanima | 29 | 10 | [6 empty] | 5
| Panchakanya, 2 PH, supermai | 25.8 | 8.5 | [6 empty] | 10
| Sagarmatha | 12.6 | 4.4 | [6 empty] | 8
| PuwaNEA | 6.2 | 3.5 | [6 empty] | 10
| Jogmai | 7.6 | 2.5 | [6 empty] | 20
| Puwa khola | 4 | 1 | [6 empty] | 15
| Himal dolaka | 8 | 0 | [6 empty] | 90
| Mai beni | 9.5 | 5.75
102.7
Ghorai | Ghorai_20MW Max | S/D | 9-10 MW 50%
| Sona | S/D
Birjung | Bir-5- industry
Bindambasini-Ind
Parsuani-Ind
Birjung-Parwani | 400 Amp
Kohal | 40.9 | 40.7 | 50.9 | 10.2
Shivpur | 8.3 | 8.3 |  | -8.3
Sunwal | 12.2 | 11.2 | 18.5 | 7.3
Butwal | 50.3 | 49.9 | 54.2 | 4.3
Mainiya | 41.2 | 38.3 | 52.6 | 14.3 |  |  |  |  | 36.7
Bard | 9.6 | 9.3 | 11.1 | 1.8
Hetauda-1 | 3 | 1.3 | 27.7 | 26.4 |  |  |  |  | 30.2
Hetauda-2 | 20.2 | 16.9 | 16.9 | 0 |  |  |  |  | 31.9
Parwani-1 | 8.4 | 0 | 25.9 | 25.9 |  |  |  |  | 19.2
Parwani- 2 | 21.9 | 0 | 22.5 | 22.5 |  |  |  |  | 4.2
Birgunj | 31.6 | 31.5 | 31.5 | 0 |  |  |  |  | 2.7
Duhabi | 106.3 | 62 | 132 | 70 |  |  |  |  | 3.7
|  |  |  | 174.4 |  |  |  |  | 128.6
Kathmandu
Chapali | 132/11 kV Transformer | 45 MVA | 218 Amp Max

## Total Industrial Load 2080
Industrial Loading (Updated 2080/10/16)
A. | Hetauda Grid Division
S.N. | Consumer Name | Supply Voltage | Substation | Recent Max Load (MW) | Substations
1 | Hetauda cement | 66 | Hetauda ss | 6.8 | Hetauda: | #REF!
2 | Hulas Steel Industries | 66 |  | 7.735 | Parwanipur: | 114.3335
3 | Jagdamba Steel | 66 |  | 34 | Birgung: | 0.34
4 | Jagadamba Wires | 66 | Parwanipur ss | 14.025 | Kamane: | 7.599
5 | Hama Iron & Steel Ind. | 66 |  | 2.55 |  | #REF!
6 | Surya Nepal | 66 |  | 1.02
7 | Jagadamba Enterprises | 66 |  | 27.2
8 | Ashok Steel | 66 |  | 11.05 |  | 80.0335
9 | Shalimar Cement | 66 |  | 2.55
10 | Triveni Spinning Mill | 66 |  | 5.525 | 193
11 | Narayani Ispat | 66 |  | 21.25 | 67
12 | Himal Iron& Steel Pvt.Ltd | 66 |  | 3.315
13 | Sarbottam steels | 66 | Parwanipur ss | 22.525
14 | Triveni Syenthetic yarn | 66 |  | 1.7
15 | Shivam Cement | 33 | Kamane ss | 12.75
16 | Riddhi Siddhi Cement | 33 |  | 12.75
17 | Hetauda Industrial State A | 11 | Hetauda ss | 1.53
18 | Hetauda Industrial State B | 11 | Kamane ss | 4.284
19 | Hetauda Industrial State C | 11 | Kamane ss | 2.8985
20 | Ncell | 11 | Dedicated feeders from hetauda ss | 0.34
21 | Industrial-1 | 11 | Bharatpur ss | 2.652
22 | Industrial -2 | 11 | Bharatpur ss | 3.7655
23 | Industrial-3 | 11 | From New-Bharatpur ss | 4.8875
24 | Coca Cola | 11 | bharatpur ss | 2.975
25 | Amlekhgunj Pole Plant | 11 | Amlekhgunj ss | 0.11305
26 | Nepal Oil Nigam | 11 | Amlekhgunj ss | 0.272
27 | Dabur | 11 | Parwanipur ss | 2.669
28 | Simara | 11 | Parwanipur ss | 5.355
29 | Jagadamba | 11 | Parwanipur ss | 5.372
30 | Narayani | 11 | Parwanipur ss | 4.93
31 | Parwanipur | 11 | Parwanipur ss | 3.9015
32 | Birgunj | 11 | Parwanipur ss | 4.369
33 | Chorni | 11 | Parwanipur ss | 4.4965
34 | Nitanpur | 11 | Parwanipur ss(with oxygen plant) | 4.9045
35 | Himal | 11 | Parwanipur ss(with oxygen plant) | 3.4765
36 | Pathaliya-1 | 11 | Piluwa ss | 1.0965
37 | Pathaliya-2 | 11 | Piluwa ss | 1.7935
38 | Parsauni | 11 | Birgunj ss | 4.2245
39 | Bindhabaseni | 11 | Birgunj ss | 5.1765
40 | Jagannathpur | 11 | Birgunj ss with very few domestic consumer | 2.8815
| Total (MW): |  |  | 265.109
B. | Duhabi Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage | Substation/DCS | Recent Max Load (MW)
1 | 11 kV Tahara1 | 11 | Duhabi | 2.8
2 | 11 kV Tahara2 | 11 | Duhabi | 4.9
3 | 11 kV Biratnagar2 | 11 | Duhabi | 5.4
4 | 11 kV Biratnagar1 | 11 | Duhabi | 5
5 | 33 kV Pashupati Iron | 33 | Duhabi | 16.5
6 | 33 kV Premier | 33 | Duhabi | 16.9
7 | 33 kV Swastik | 33 | Duhabi | 13.05
8 | 33 kv Multifuel 2 | 33 | Duhabi | 4.7
9 | 33 kv Duhabi Industries | 33 | Duhabi | 21.15
10 | 33 kv Biratnagar Industries | 33 | Duhabi | 13.5
11 | 33 kv Reliance | 33 | Khanar | 11.5
12 | 11 kv Purano Udyog | 11 | Khanar | 4.5
13 | 11 kv Udyog | 11 | Inaruwa | 3
14 | 33 kv Arati | 33 | Tanki SS | 9.55
15 | 11 kv Tanki | 11 | Basbari SS | 3.5
16 | 11 kv Hatimuda | 11 | Basbari SS | 3.6
17 | 11 kv Judi | 11 | Katahari SS | 4.1
18 | 11 kv Singya | 11 | Katahari SS | 2.6
19 | 33 kv RJM | 33 | Rani SS | 0.9
20 | 11 KV BJM | 11 | Rani SS | 2.1667
| Total (MW): |  |  | 149.3167
C. | Kathmandu Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage | Substation | Recent Max Load (MW)
1 | Patan Industrial District | 11 | Balaju | 3
2 | Balaju Industrial District | 11 | Patan | 7.7
3 | Bhaktapur Industrial District | 11 | Bhaktapur | 1.1
4 | Huaxin Cement Narayani Pvt.Ltd. | 132 | Malekhu | 6
5 | United Cement | 33 | Naubise DC SS | 1.5
| Total (MW): |  |  | 19.3
D. | Pokhara Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage | Substation | Recent Max Load (MW)
1 | Pokhara Industrial District | 11 | Pokhara | 2
| Total |  |  | 2
E. | Butwal Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage | DC/Substation | Recent Max Load (MW)
1 | 33 KV Ghorahi Cement | 132/33 | Ghorahi | 12.76
2 | 33 KV Sonapur |  |  | 3.052
3 | 33 KV Samrat Cement | 132/33 | Lamahi | 2.4925
4 | 33 KV Agni Cement |  |  | 0.19329
5 | 33 KV Vijaya Shree Steel | 132/33 | Chanauta | 17.6
6 | 33 KV Industrial |  |  | 5.8345
7 | 33 KV Dhakadhai I (Shree Steel) | 132/33 | Butwal | 9.156
8 | 33 KV Dhakadhai II (Shree Steel)
9 | 33 KV Bhairahawa New II |  |  | 1.2208
10 | 33 KV Bhairahawa Old |  |  | 8.1387
11 | 33 KV Groud water |  |  | 8.6474
12 | 33 KV Laxmi Steel | 132/33 | Sunwal | 21.1098
13 | 33 KV Palpa Cement |  |  | 13.0983
14 | 33 KV Sarbottam Cement |  |  | 9.9852
15 | 33 KV Goyal Spat |  |  | 13.3272
16 | 132 KV Hongshi Cement | 132 | Bardaghat | 13.2
17 | 11 KV CG Cement | 132/11 |  | 3.2707
18 | 11 KV Industrial |  |  | 1.4667
19 | 33 KV Industrial I | 132/33 | Gandak | 7.04
20 | 33 KV Industrial II |  |  | 4.4
21 | 33 KV Arghakhanchi Cement | 132/33 | Mainahiya | 12.9711
22 | 33 KV Bhairahawa -I |  |  | 7.3249
23 | 33 KV Bhairahawa -II |  |  | 18.3121
24 | 33 KV New -II |  |  | 6.3584
25 | 33 KV Bhairahawa Old |  |  | 15.4636
26 | 33 KV Lumbini |  |  | 10.2751
| Total (MW): |  |  | 226.6983
F. | Dhalkebar Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage, kV | Substation | Recent Max Load (MW)
1 | Cosmos Cement | 33 | Dhalkebar S/S | 4.7
2 | Everest Paper Mill | 33 | Dhalkebar S/S | 2
3 | Everest Sugar Mill | 33 | Dhalkebar S/S | 0.34
4 | 11 kV Industrial (Dhalkebar, small industries) | 11 | Dhalkebar S/S | 2.04
5 | Saurya Cement | 132 | Mirchaiya S/S | 11.7
6 | Maruti Cement | 33 | Mirchaiya S/S | 9
7 | Udaypur Cement | 11 | Jaljale S/S from Lahan | 5.5
8 | InduShankar Sugar Mill, Bagmati Sinchai, karmahiya Khanepani | 33 | Nawalpur S/S | 1.3
9 | Godawari Steels | 33 | Chapur S/S | 1
| Total (MW): |  |  | 37.58
G. | Attariya Grid Division
S.N. | Consumer/Feeder Name | Supply Voltage | Substation | Recent Max Load (MW)
1 | Industrial Feeder | 11 | Kohalpur | 4
2 | Ambe steel | 33 | Kohalpur | 30
| Total (MW): |  |  | 34
| Total Industrial Load in MW without considering Diversity Factor |  |  | Recent Max Load (MW)
734.004
Note: | Diversity Factor to be considered
| Total Industrial Load in MW considering Coincedence Factor of 0.75 |  |  | Recent Max Load (MW)
550.503

## Sheet8
0 | 0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.22917 | 0.25 | 0.27083 | 0.29167 | 0.3125 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5 | 0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.72917 | 0.75 | 0.77083 | 0.79167 | 0.8125 | 0.83333 | 0.85417 | 0.875 | 0.91667 | 0.95833
1157.29 | 1199.29 | 1160.89 | 1167.69 | 1185.19 | 1224.89 | 1342.59 | 1325.69 | 1572.71 | 1507.31 | 1529.89 | 1791.09 | 1589.59 | 1584.99 | 1388.19 | 1496.79 | 1479.59 | 1473.09 | 1503.79 | 1462.49 | 1331.69 | 1528.69 | 1707.19 | 1808.99 | 1770.95 | 1743.29 | 1697.99 | 1746.59 | 1542.79 | 1362.29 | 1233.09
1190.79 | 1194.69 | 1151.29 | 1149.89 | 1168.69 | 1266.59 | 1340.39 | 1433.79 | 1588.89 | 1719.89 | 1795.79 | 1717.59 | 1704.09 | 1650.79 | 1577.19 | 1558.19 | 1565.99 | 1525.59 | 1601.59 | 1503.59 | 1307.49 | 1513.99 | 1672.89 | 1847.19 | 1803.85 | 1728.09 | 1683.59 | 1649.79 | 1353.99 | 1355.69 | 1268.99
1211.89 | 1196.34 | 1193.97 | 1180.96 | 1199.79 | 1205.69 | 1262.29 | 1368.49 | 1522.99 | 1558.99 | 1666.49 | 1689.99 | 1538.19 | 1572.69 | 1638.09 | 1545.99 | 1462.99 | 1514.19 | 1528.99 | 1484.89 | 1543.79 | 1551.89 | 1642.39 | 1691.79 | 1805.59 | 1693.99 | 1624.69 | 1581.99 | 1490.09 | 1326.39 | 1280.39
1207.79 | 1182.09 | 1154.29 | 1139.49 | 1155.19 | 1186.79 | 1254.19 | 1372.39 | 1461.49 | 1500.59 | 1646.99 | 1675.99 | 1597.09 | 1554.79 | 1500.59 | 1426.59 | 1472.59 | 1459.29 | 1523.23 | 1570.03 | 1483.19 | 1570.29 | 1625.49 | 1788.05 | 1787.25 | 1723.89 | 1596.89 | 1512.89 | 1502.69 | 1363.29 | 1279.89